## WQ Performance
Region Name | System Name | Parameter | Units | Health Guideline * | Aesthetic Guideline * | Average Value | Health Compliance # | Disinfection | End Date | Comment
Eyre | Coffin Bay | Alkalinity | mg/L | NG | NG | 220 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Arsenic | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Barium | mg/L | ≤ 2 | NG | 0.0089 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Bicarbonate | mg/L | NG | NG | 269 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Boron | mg/L | ≤ 4 | NG | 0.176 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Calcium | mg/L | NG | NG | 44.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chloride | mg/L | NG | ≤ 250 | 110 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Chromium | mg/L | ≤ 0.05 | NG | 0.0032 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0046 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Fluoride | mg/L | ≤ 1.5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Hardness | mg/L | NG | ≤ 200 | 248 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Iron | mg/L | NG | ≤ 0.3 | < 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Magnesium | mg/L | NG | NG | 33.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Nickel | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 6.21 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Potassium | mg/L | NG | NG | 5.77 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Selenium | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Silica - reactive | mg/L | NG | ≤ 80 | 8.33 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Sodium | mg/L | NG | ≤ 180 | 68.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Sulphate | mg/L | NG | ≤ 250 | 21.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Total dissolved solids | mg/L | NG | ≤ 600 | 451 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 12 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Uranium | mg/L | ≤ 0.02 | NG | 0.0010 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Zinc | mg/L | NG | ≤ 3 | 0.0050 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Hardness - English Degrees | °e | NG | NG | 17.36 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Hardness - French Degrees | °f | NG | NG | 24.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Hardness - German Degrees | °dH | NG | NG | 13.89 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Coffin Bay | Hardness - International | PPM or mg/L | NG | NG | 248 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Alkalinity | mg/L | NG | NG | 229 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Arsenic | mg/L | ≤ 0.01 | NG | 0.00181 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Barium | mg/L | ≤ 2 | NG | 0.0095 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Bicarbonate | mg/L | NG | NG | 279 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Boron | mg/L | ≤ 4 | NG | 0.127 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Calcium | mg/L | NG | NG | 59.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chloride | mg/L | NG | ≤ 250 | 211 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Chromium | mg/L | ≤ 0.05 | NG | 0.0037 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0053 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Hardness | mg/L | NG | ≤ 200 | 283 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Iron | mg/L | NG | ≤ 0.3 | < 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Magnesium | mg/L | NG | NG | 32.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Nickel | mg/L | ≤ 0.02 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 13.62 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | pH | pH units | NG | 6.5 - 8.5 | 7.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Potassium | mg/L | NG | NG | 4.19 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Selenium | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Silica - reactive | mg/L | NG | ≤ 80 | 9.43 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Sodium | mg/L | NG | ≤ 180 | 122 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Sulphate | mg/L | NG | ≤ 250 | 34.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Total dissolved solids | mg/L | NG | ≤ 600 | 664 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Uranium | mg/L | ≤ 0.02 | NG | 0.0021 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Zinc | mg/L | NG | ≤ 3 | 0.0093 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Hardness - English Degrees | °e | NG | NG | 19.81 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Hardness - French Degrees | °f | NG | NG | 28.3 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Hardness - German Degrees | °dH | NG | NG | 15.85 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Elliston | Hardness - International | PPM or mg/L | NG | NG | 283 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Alkalinity | mg/L | NG | NG | 233 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Arsenic | mg/L | ≤ 0.01 | NG | 0.00060 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Barium | mg/L | ≤ 2 | NG | 0.0195 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Bicarbonate | mg/L | NG | NG | 284 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Boron | mg/L | ≤ 4 | NG | 0.079 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Calcium | mg/L | NG | NG | 72.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chloride | mg/L | NG | ≤ 250 | 168 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Chromium | mg/L | ≤ 0.05 | NG | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0118 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Fluoride | mg/L | ≤ 1.5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Hardness | mg/L | NG | ≤ 200 | 276 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Iron | mg/L | NG | ≤ 0.3 | 0.0016 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Magnesium | mg/L | NG | NG | 22.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Mercury | mg/L | ≤ 0.001 | NG | 0.00005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Nickel | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 15.67 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Potassium | mg/L | NG | NG | 2.89 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Selenium | mg/L | ≤ 0.01 | NG | 0.0010 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Silica - reactive | mg/L | NG | ≤ 80 | 10.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Sodium | mg/L | NG | ≤ 180 | 103.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Sulphate | mg/L | NG | ≤ 250 | 26.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Total dissolved solids | mg/L | NG | ≤ 600 | 589 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 20 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Uranium | mg/L | ≤ 0.02 | NG | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Zinc | mg/L | NG | ≤ 3 | 0.0117 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Hardness - English Degrees | °e | NG | NG | 19.32 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Hardness - French Degrees | °f | NG | NG | 27.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Hardness - German Degrees | °dH | NG | NG | 15.46 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South | Hardness - International | PPM or mg/L | NG | NG | 276 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Eyre South/Morgan | Alkalinity | mg/L | NG | NG | 164 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.011 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Arsenic | mg/L | ≤ 0.01 | NG | 0.00054 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Barium | mg/L | ≤ 2 | NG | 0.0276 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Bicarbonate | mg/L | NG | NG | 200 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Boron | mg/L | ≤ 4 | NG | 0.058 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Calcium | mg/L | NG | NG | 55.7 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chloral hydrate | µg/L | ≤ 100 | NG | 8.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chloride | mg/L | NG | ≤ 250 | 118 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Chromium | mg/L | ≤ 0.05 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0110 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Dichloroacetic acid | µg/L | ≤ 100 | NG | 27 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Hardness | mg/L | NG | ≤ 200 | 200 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Iron | mg/L | NG | ≤ 0.3 | 0.0037 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Magnesium | mg/L | NG | NG | 14.8 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 10.00 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Potassium | mg/L | NG | NG | 3.88 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Selenium | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Silica - reactive | mg/L | NG | ≤ 80 | 8.32 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Sodium | mg/L | NG | ≤ 180 | 78.3 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Sulphate | mg/L | NG | ≤ 250 | 40.5 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Total dissolved solids | mg/L | NG | ≤ 600 | 440 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Trichloroacetic acid | µg/L | ≤ 100 | NG | 15 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 189 | 82.9% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Uranium | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Zinc | mg/L | NG | ≤ 3 | 0.0076 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Hardness - English Degrees | °e | NG | NG | 14.00 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Hardness - French Degrees | °f | NG | NG | 20.0 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Hardness - German Degrees | °dH | NG | NG | 11.20 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Eyre South/Morgan | Hardness - International | PPM or mg/L | NG | NG | 200 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Treatment and Fluoridation on River Murray source water only.
Eyre | Morgan/Eyre | Alkalinity | mg/L | NG | NG | 61 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.020 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Arsenic | mg/L | ≤ 0.01 | NG | 0.00050 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Barium | mg/L | ≤ 2 | NG | 0.0421 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Bicarbonate | mg/L | NG | NG | 75 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Boron | mg/L | ≤ 4 | NG | 0.021 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Calcium | mg/L | NG | NG | 21.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chloral hydrate | µg/L | ≤ 100 | NG | 33.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chloride | mg/L | NG | ≤ 250 | 49 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chloroacetic acid | µg/L | ≤ 150 | NG | 7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0204 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Dichloroacetic acid | µg/L | ≤ 100 | NG | 67 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Hardness | mg/L | NG | ≤ 200 | 80 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Iron | mg/L | NG | ≤ 0.3 | 0.0438 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Lead | mg/L | ≤ 0.01 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Magnesium | mg/L | NG | NG | 6.04 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0038 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 2.17 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Potassium | mg/L | NG | NG | 5.57 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Silica - reactive | mg/L | NG | ≤ 80 | 4.00 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Sodium | mg/L | NG | ≤ 180 | 48.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Sulphate | mg/L | NG | ≤ 250 | 59.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Total dissolved solids | mg/L | NG | ≤ 600 | 245 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Trichloroacetic acid | µg/L | ≤ 100 | NG | 38 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 157 | 91.7% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Turbidity | NTU | NG | ≤ 5 | 0.52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Zinc | mg/L | NG | ≤ 3 | 0.0092 | NA | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Hardness - English Degrees | °e | NG | NG | 5.60 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Hardness - French Degrees | °f | NG | NG | 8.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Hardness - German Degrees | °dH | NG | NG | 4.48 | NG | Chlorine | 01/04/2022 - 31/03/2023
Eyre | Morgan/Eyre | Hardness - International | PPM or mg/L | NG | NG | 80 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Alkalinity | mg/L | NG | NG | 51 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.029 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Barium | mg/L | ≤ 2 | NG | 0.0407 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Bicarbonate | mg/L | NG | NG | 62 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Boron | mg/L | ≤ 4 | NG | 0.025 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Calcium | mg/L | NG | NG | 21.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chloral hydrate | µg/L | ≤ 100 | NG | 8.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chloride | mg/L | NG | ≤ 250 | 52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0043 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Dichloroacetic acid | µg/L | ≤ 100 | NG | 7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Fluoride | mg/L | ≤ 1.5 | NG | 0.45 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Hardness | mg/L | NG | ≤ 200 | 88 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Iron | mg/L | NG | ≤ 0.3 | 0.0067 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Magnesium | mg/L | NG | NG | 8.52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Nickel | mg/L | ≤ 0.02 | NG | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.11 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Potassium | mg/L | NG | NG | 5.02 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Silica - reactive | mg/L | NG | ≤ 80 | 5.53 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Sodium | mg/L | NG | ≤ 180 | 36.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Sulphate | mg/L | NG | ≤ 250 | 58.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Total dissolved solids | mg/L | NG | ≤ 600 | 224 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Trichloroacetic acid | µg/L | ≤ 100 | NG | 23 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 118 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Zinc | mg/L | NG | ≤ 3 | 0.0022 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Hardness - English Degrees | °e | NG | NG | 6.16 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Hardness - French Degrees | °f | NG | NG | 8.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Hardness - German Degrees | °dH | NG | NG | 4.93 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Anstey Hill (supplying north eastern Adelaide) | Hardness - International | PPM or mg/L | NG | NG | 88 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Alkalinity | mg/L | NG | NG | 52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.025 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Arsenic | mg/L | ≤ 0.01 | NG | 0.00038 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Barium | mg/L | ≤ 2 | NG | 0.0305 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Bicarbonate | mg/L | NG | NG | 64 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Calcium | mg/L | NG | NG | 20.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chloral hydrate | µg/L | ≤ 100 | NG | 7.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chloride | mg/L | NG | ≤ 250 | 101 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Colour | HU | NG | ≤ 15 | 2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0067 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Dichloroacetic acid | µg/L | ≤ 100 | NG | 16 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Hardness | mg/L | NG | ≤ 200 | 101 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Iron | mg/L | NG | ≤ 0.3 | 0.0040 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Magnesium | mg/L | NG | NG | 12.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Mercury | mg/L | ≤ 0.001 | NG | 0.00036 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.24 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Potassium | mg/L | NG | NG | 3.82 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Silica - reactive | mg/L | NG | ≤ 80 | 3.51 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Sodium | mg/L | NG | ≤ 180 | 59.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Sulphate | mg/L | NG | ≤ 250 | 35.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Total dissolved solids | mg/L | NG | ≤ 600 | 311 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Trichloroacetic acid | µg/L | ≤ 100 | NG | 18 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 141 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Uranium | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Zinc | mg/L | NG | ≤ 3 | 0.0026 | NA | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Hardness - English Degrees | °e | NG | NG | 7.07 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Hardness - French Degrees | °f | NG | NG | 10.1 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Hardness - German Degrees | °dH | NG | NG | 5.66 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Barossa (supplying Gawler and surrounds) | Hardness - International | PPM or mg/L | NG | NG | 101 | NG | Chlorine | 01/04/2022 - 31/03/2023
Metropolitan | Central metro Adelaide suburbs | Alkalinity | mg/L | NG | NG | 58 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.036 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Arsenic | mg/L | ≤ 0.01 | NG | 0.00032 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Barium | mg/L | ≤ 2 | NG | 0.0302 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Bicarbonate | mg/L | NG | NG | 70 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Boron | mg/L | ≤ 4 | NG | 0.051 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Calcium | mg/L | NG | NG | 24.9 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chloral hydrate | µg/L | ≤ 100 | NG | 10.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chloride | mg/L | NG | ≤ 250 | 80 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0537 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Dichloroacetic acid | µg/L | ≤ 100 | NG | 13 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | E. coli | per cent compliance | 0 | NG | 99.9% | 99.9% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Hardness | mg/L | NG | ≤ 200 | 116 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Iron | mg/L | NG | ≤ 0.3 | 0.0130 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Magnesium | mg/L | NG | NG | 12.94 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.26 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Potassium | mg/L | NG | NG | 4.95 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Silica - reactive | mg/L | NG | ≤ 80 | 2.24 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Sodium | mg/L | NG | ≤ 180 | 44.8 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Sulphate | mg/L | NG | ≤ 250 | 47.1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Total dissolved solids | mg/L | NG | ≤ 600 | 260 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Trichloroacetic acid | µg/L | ≤ 100 | NG | 15 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 158 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Zinc | mg/L | NG | ≤ 3 | 0.0059 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Hardness - English Degrees | °e | NG | NG | 8.12 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Hardness - French Degrees | °f | NG | NG | 11.6 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Hardness - German Degrees | °dH | NG | NG | 6.50 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Central metro Adelaide suburbs | Hardness - International | PPM or mg/L | NG | NG | 116 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Alkalinity | mg/L | NG | NG | 57 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.037 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Barium | mg/L | ≤ 2 | NG | 0.0339 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Bicarbonate | mg/L | NG | NG | 69 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Boron | mg/L | ≤ 4 | NG | 0.059 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Calcium | mg/L | NG | NG | 24.1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chloral hydrate | µg/L | ≤ 100 | NG | 13.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chloride | mg/L | NG | ≤ 250 | 72 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0214 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Dichloroacetic acid | µg/L | ≤ 100 | NG | 9 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Fluoride | mg/L | ≤ 1.5 | NG | 0.61 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Hardness | mg/L | NG | ≤ 200 | 107 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Iron | mg/L | NG | ≤ 0.3 | 0.0582 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Magnesium | mg/L | NG | NG | 11.36 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0019 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.366 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Potassium | mg/L | NG | NG | 4.89 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Silica - reactive | mg/L | NG | ≤ 80 | 4.82 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Sodium | mg/L | NG | ≤ 180 | 43.4 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Sulphate | mg/L | NG | ≤ 250 | 48.0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Total dissolved solids | mg/L | NG | ≤ 600 | 263 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Trichloroacetic acid | µg/L | ≤ 100 | NG | 17 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 156 | 99.0% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Turbidity | NTU | NG | ≤ 5 | 0.12 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Zinc | mg/L | NG | ≤ 3 | 0.0055 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Hardness - English Degrees | °e | NG | NG | 7.49 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Hardness - French Degrees | °f | NG | NG | 10.7 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Hardness - German Degrees | °dH | NG | NG | 5.99 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Eastern metro Adelaide suburbs | Hardness - International | PPM or mg/L | NG | NG | 107 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Alkalinity | mg/L | NG | NG | 76 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.055 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.28 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Arsenic | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Barium | mg/L | ≤ 2 | NG | 0.0233 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Bicarbonate | mg/L | NG | NG | 83 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Boron | mg/L | ≤ 4 | NG | 0.035 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Calcium | mg/L | NG | NG | 26.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Carbonate | mg/L | NG | NG | 5 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Chloride | mg/L | NG | ≤ 250 | 152 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Colour | HU | NG | ≤ 15 | 3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0149 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Fluoride | mg/L | ≤ 1.5 | NG | 0.73 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Hardness | mg/L | NG | ≤ 200 | 129 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Iron | mg/L | NG | ≤ 0.3 | 0.0075 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Magnesium | mg/L | NG | NG | 15.1 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0043 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Mercury | mg/L | ≤ 0.001 | NG | 0.00010 | 94.7% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.48 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | pH | pH units | NG | 6.5 - 8.5 | 8.7 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Potassium | mg/L | NG | NG | 6.85 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Silica - reactive | mg/L | NG | ≤ 80 | 2.14 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Sodium | mg/L | NG | ≤ 180 | 102 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Sulphate | mg/L | NG | ≤ 250 | 64.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Total dissolved solids | mg/L | NG | ≤ 600 | 451 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 109 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Zinc | mg/L | NG | ≤ 3 | 0.0017 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Hardness - English Degrees | °e | NG | NG | 9.02 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Hardness - French Degrees | °f | NG | NG | 12.9 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Hardness - German Degrees | °dH | NG | NG | 7.25 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Myponga metro (supplying outer southern Adelaide) | Hardness - International | PPM or mg/L | NG | NG | 129 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Metropolitan | Northern metro Adelaide suburbs | Alkalinity | mg/L | NG | NG | 58 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.029 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Barium | mg/L | ≤ 2 | NG | 0.0375 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Bicarbonate | mg/L | NG | NG | 71 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Boron | mg/L | ≤ 4 | NG | 0.023 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Calcium | mg/L | NG | NG | 22.7 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chloral hydrate | µg/L | ≤ 100 | NG | 9.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chloride | mg/L | NG | ≤ 250 | 72 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0083 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Dichloroacetic acid | µg/L | ≤ 100 | NG | 8 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Fluoride | mg/L | ≤ 1.5 | NG | 0.34 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Hardness | mg/L | NG | ≤ 200 | 103 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Iron | mg/L | NG | ≤ 0.3 | 0.0073 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Magnesium | mg/L | NG | NG | 11.26 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.48 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Potassium | mg/L | NG | NG | 4.60 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Silica - reactive | mg/L | NG | ≤ 80 | 4.34 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Sodium | mg/L | NG | ≤ 180 | 45.7 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Sulphate | mg/L | NG | ≤ 250 | 46.0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Total dissolved solids | mg/L | NG | ≤ 600 | 280 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Trichloroacetic acid | µg/L | ≤ 100 | NG | 18 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 139 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Zinc | mg/L | NG | ≤ 3 | 0.0028 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Hardness - English Degrees | °e | NG | NG | 7.21 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Hardness - French Degrees | °f | NG | NG | 10.3 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Hardness - German Degrees | °dH | NG | NG | 5.77 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Northern metro Adelaide suburbs | Hardness - International | PPM or mg/L | NG | NG | 103 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Alkalinity | mg/L | NG | NG | 60 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.038 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Arsenic | mg/L | ≤ 0.01 | NG | 0.00035 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Barium | mg/L | ≤ 2 | NG | 0.0306 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Bicarbonate | mg/L | NG | NG | 73 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Boron | mg/L | ≤ 4 | NG | 0.050 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Calcium | mg/L | NG | NG | 25.6 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chloral hydrate | µg/L | ≤ 100 | NG | 19.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chloride | mg/L | NG | ≤ 250 | 81 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0328 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Dichloroacetic acid | µg/L | ≤ 100 | NG | 13 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Hardness | mg/L | NG | ≤ 200 | 117 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Iron | mg/L | NG | ≤ 0.3 | 0.0042 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Magnesium | mg/L | NG | NG | 12.9 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.61 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | pH | pH units | NG | 6.5 - 8.5 | 7.3 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Potassium | mg/L | NG | NG | 5.15 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Silica - reactive | mg/L | NG | ≤ 80 | 1.86 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Sodium | mg/L | NG | ≤ 180 | 48.0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Sulphate | mg/L | NG | ≤ 250 | 48.0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Total dissolved solids | mg/L | NG | ≤ 600 | 277 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Trichloroacetic acid | µg/L | ≤ 100 | NG | 25 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 162 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Zinc | mg/L | NG | ≤ 3 | 0.0045 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Hardness - English Degrees | °e | NG | NG | 8.19 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Hardness - French Degrees | °f | NG | NG | 11.7 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Hardness - German Degrees | °dH | NG | NG | 6.55 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Southern metro Adelaide suburbs | Hardness - International | PPM or mg/L | NG | NG | 117 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Alkalinity | mg/L | NG | NG | 66 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.033 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Arsenic | mg/L | ≤ 0.01 | NG | 0.00031 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Barium | mg/L | ≤ 2 | NG | 0.0330 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Bicarbonate | mg/L | NG | NG | 80 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Boron | mg/L | ≤ 4 | NG | 0.036 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Calcium | mg/L | NG | NG | 25.9 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chloral hydrate | µg/L | ≤ 100 | NG | 11.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chloride | mg/L | NG | ≤ 250 | 82 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0205 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Dichloroacetic acid | µg/L | ≤ 100 | NG | 9 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Hardness | mg/L | NG | ≤ 200 | 124 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Iron | mg/L | NG | ≤ 0.3 | 0.0138 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Magnesium | mg/L | NG | NG | 14.29 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.47 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | pH | pH units | NG | 6.5 - 8.5 | 7.2 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Potassium | mg/L | NG | NG | 4.91 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Silica - reactive | mg/L | NG | ≤ 80 | 3.74 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Sodium | mg/L | NG | ≤ 180 | 46.7 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Sulphate | mg/L | NG | ≤ 250 | 50.5 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Total dissolved solids | mg/L | NG | ≤ 600 | 285 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Trichloroacetic acid | µg/L | ≤ 100 | NG | 21 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 164 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Zinc | mg/L | NG | ≤ 3 | 0.0045 | NA | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Hardness - English Degrees | °e | NG | NG | 8.68 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Hardness - French Degrees | °f | NG | NG | 12.4 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Hardness - German Degrees | °dH | NG | NG | 6.94 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Metropolitan | Western metro Adelaide suburbs | Hardness - International | PPM or mg/L | NG | NG | 124 | NG | Chlorine | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Northern | Barmera | Alkalinity | mg/L | NG | NG | 65 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.017 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Arsenic | mg/L | ≤ 0.01 | NG | 0.00047 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Barium | mg/L | ≤ 2 | NG | 0.0513 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Bicarbonate | mg/L | NG | NG | 79 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Boron | mg/L | ≤ 4 | NG | 0.027 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Calcium | mg/L | NG | NG | 17.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chloral hydrate | µg/L | ≤ 100 | NG | 20.9 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chloride | mg/L | NG | ≤ 250 | 35 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.6 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0716 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Dichloroacetic acid | µg/L | ≤ 100 | NG | 22 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Hardness | mg/L | NG | ≤ 200 | 77 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Iron | mg/L | NG | ≤ 0.3 | 0.0082 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Magnesium | mg/L | NG | NG | 8.02 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0033 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Nickel | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.45 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Potassium | mg/L | NG | NG | 6.45 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Silica - reactive | mg/L | NG | ≤ 80 | 7.73 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Sodium | mg/L | NG | ≤ 180 | 41.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Sulphate | mg/L | NG | ≤ 250 | 60.2 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Total dissolved solids | mg/L | NG | ≤ 600 | 212 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Trichloroacetic acid | µg/L | ≤ 100 | NG | 44 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 159 | 92.3% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Turbidity | NTU | NG | ≤ 5 | 0.12 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Zinc | mg/L | NG | ≤ 3 | 0.0102 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Hardness - English Degrees | °e | NG | NG | 5.39 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Hardness - French Degrees | °f | NG | NG | 7.7 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Hardness - German Degrees | °dH | NG | NG | 4.31 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Barmera | Hardness - International | PPM or mg/L | NG | NG | 77 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Alkalinity | mg/L | NG | NG | 66 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.016 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Arsenic | mg/L | ≤ 0.01 | NG | 0.00055 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Barium | mg/L | ≤ 2 | NG | 0.0509 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Bicarbonate | mg/L | NG | NG | 81 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Boron | mg/L | ≤ 4 | NG | 0.029 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Calcium | mg/L | NG | NG | 16.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chloral hydrate | µg/L | ≤ 100 | NG | 15.4 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chloride | mg/L | NG | ≤ 250 | 36 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0375 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Dichloroacetic acid | µg/L | ≤ 100 | NG | 26 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Hardness | mg/L | NG | ≤ 200 | 75 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Iron | mg/L | NG | ≤ 0.3 | 0.1136 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Lead | mg/L | ≤ 0.01 | NG | 0.0007 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Magnesium | mg/L | NG | NG | 8.14 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0057 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Nickel | mg/L | ≤ 0.02 | NG | 0.0016 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Potassium | mg/L | NG | NG | 6.04 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Silica - reactive | mg/L | NG | ≤ 80 | 4.99 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Silver | mg/L | ≤ 0.1 | NG | 0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Sodium | mg/L | NG | ≤ 180 | 40.9 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Sulphate | mg/L | NG | ≤ 250 | 57.1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Total dissolved solids | mg/L | NG | ≤ 600 | 227 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Trichloroacetic acid | µg/L | ≤ 100 | NG | 28 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 137 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Turbidity | NTU | NG | ≤ 5 | 0.14 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Zinc | mg/L | NG | ≤ 3 | 0.0443 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Hardness - English Degrees | °e | NG | NG | 5.25 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Hardness - French Degrees | °f | NG | NG | 7.5 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Hardness - German Degrees | °dH | NG | NG | 4.20 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Berri | Hardness - International | PPM or mg/L | NG | NG | 75 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Alkalinity | mg/L | NG | NG | 87 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.015 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Arsenic | mg/L | ≤ 0.01 | NG | 0.00052 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Barium | mg/L | ≤ 2 | NG | 0.0504 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Bicarbonate | mg/L | NG | NG | 106 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Boron | mg/L | ≤ 4 | NG | 0.030 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Calcium | mg/L | NG | NG | 18.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chloral hydrate | µg/L | ≤ 100 | NG | 19.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chloride | mg/L | NG | ≤ 250 | 50 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0636 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Dichloroacetic acid | µg/L | ≤ 100 | NG | 29 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Hardness | mg/L | NG | ≤ 200 | 81 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Iron | mg/L | NG | ≤ 0.3 | 0.0136 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Magnesium | mg/L | NG | NG | 8.51 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0016 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Nickel | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.86 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Potassium | mg/L | NG | NG | 6.81 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Silica - reactive | mg/L | NG | ≤ 80 | 3.64 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Sodium | mg/L | NG | ≤ 180 | 35.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Sulphate | mg/L | NG | ≤ 250 | 7.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Total dissolved solids | mg/L | NG | ≤ 600 | 197 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Trichloroacetic acid | µg/L | ≤ 100 | NG | 22 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 136 | 92.9% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Turbidity | NTU | NG | ≤ 5 | 0.25 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Zinc | mg/L | NG | ≤ 3 | 0.0063 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Hardness - English Degrees | °e | NG | NG | 5.67 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Hardness - French Degrees | °f | NG | NG | 8.1 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Hardness - German Degrees | °dH | NG | NG | 4.54 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Blanchetown | Hardness - International | PPM or mg/L | NG | NG | 81 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Alkalinity | mg/L | NG | NG | 88 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.014 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Arsenic | mg/L | ≤ 0.01 | NG | 0.00048 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Barium | mg/L | ≤ 2 | NG | 0.0448 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Bicarbonate | mg/L | NG | NG | 107 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Boron | mg/L | ≤ 4 | NG | 0.022 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Calcium | mg/L | NG | NG | 16.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chloral hydrate | µg/L | ≤ 100 | NG | 23.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chloride | mg/L | NG | ≤ 250 | 47 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0200 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Dichloroacetic acid | µg/L | ≤ 100 | NG | 38 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Hardness | mg/L | NG | ≤ 200 | 74 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Iron | mg/L | NG | ≤ 0.3 | 0.0030 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Lead | mg/L | ≤ 0.01 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Magnesium | mg/L | NG | NG | 8.22 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0017 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.54 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Potassium | mg/L | NG | NG | 6.17 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Silica - reactive | mg/L | NG | ≤ 80 | 1.94 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Sodium | mg/L | NG | ≤ 180 | 35.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Sulphate | mg/L | NG | ≤ 250 | 6.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Total dissolved solids | mg/L | NG | ≤ 600 | 192 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Trichloroacetic acid | µg/L | ≤ 100 | NG | 54 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 123 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Zinc | mg/L | NG | ≤ 3 | 0.0043 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Hardness - English Degrees | °e | NG | NG | 5.18 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Hardness - French Degrees | °f | NG | NG | 7.4 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Hardness - German Degrees | °dH | NG | NG | 4.14 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Cadell | Hardness - International | PPM or mg/L | NG | NG | 74 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Alkalinity | mg/L | NG | NG | 88 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.014 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Arsenic | mg/L | ≤ 0.01 | NG | 0.00054 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Barium | mg/L | ≤ 2 | NG | 0.0427 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Bicarbonate | mg/L | NG | NG | 107 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Calcium | mg/L | NG | NG | 17.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chloral hydrate | µg/L | ≤ 100 | NG | 29.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chloride | mg/L | NG | ≤ 250 | 44 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chloroacetic acid | µg/L | ≤ 150 | NG | 5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0031 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Dichloroacetic acid | µg/L | ≤ 100 | NG | 59 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Hardness | mg/L | NG | ≤ 200 | 76 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Iron | mg/L | NG | ≤ 0.3 | 0.0132 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Magnesium | mg/L | NG | NG | 7.66 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.19 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Potassium | mg/L | NG | NG | 6.48 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Silica - reactive | mg/L | NG | ≤ 80 | 1.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Sodium | mg/L | NG | ≤ 180 | 32.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Sulphate | mg/L | NG | ≤ 250 | 5.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Total dissolved solids | mg/L | NG | ≤ 600 | 177 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Trichloroacetic acid | µg/L | ≤ 100 | NG | 62 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 107 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Turbidity | NTU | NG | ≤ 5 | 0.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Zinc | mg/L | NG | ≤ 3 | 0.0039 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Hardness - English Degrees | °e | NG | NG | 5.32 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Hardness - French Degrees | °f | NG | NG | 7.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Hardness - German Degrees | °dH | NG | NG | 4.26 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Glossop | Hardness - International | PPM or mg/L | NG | NG | 76 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Alkalinity | mg/L | NG | NG | 44 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.030 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Barium | mg/L | ≤ 2 | NG | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Bicarbonate | mg/L | NG | NG | 46 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Boron | mg/L | ≤ 4 | NG | 0.428 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Calcium | mg/L | NG | NG | 2.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Carbonate | mg/L | NG | NG | 4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chloride | mg/L | NG | ≤ 250 | 31 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Hardness | mg/L | NG | ≤ 200 | 4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Iron | mg/L | NG | ≤ 0.3 | 0.0118 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Lead | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Magnesium | mg/L | NG | NG | 0.12 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.38 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | pH | pH units | NG | 6.5 - 8.5 | 8.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Potassium | mg/L | NG | NG | 0.22 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Silica - reactive | mg/L | NG | ≤ 80 | 0.93 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Sodium | mg/L | NG | ≤ 180 | 35.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Sulphate | mg/L | NG | ≤ 250 | 2.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Total dissolved solids | mg/L | NG | ≤ 600 | 103 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | <4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Zinc | mg/L | NG | ≤ 3 | 0.0025 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Hardness - English Degrees | °e | NG | NG | 0.28 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Hardness - French Degrees | °f | NG | NG | 0.4 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Hardness - German Degrees | °dH | NG | NG | 0.22 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Leigh Creek | Hardness - International | PPM or mg/L | NG | NG | 4 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Loxton | Alkalinity | mg/L | NG | NG | 63 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.014 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.25 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Arsenic | mg/L | ≤ 0.01 | NG | 0.00050 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Barium | mg/L | ≤ 2 | NG | 0.0506 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Bicarbonate | mg/L | NG | NG | 65 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Calcium | mg/L | NG | NG | 13.35 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Carbonate | mg/L | NG | NG | 6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Chloride | mg/L | NG | ≤ 250 | 31 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 4.0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Chlorine (total residual) | mg/L | ≤ 5 | NG | 4.0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Colour | HU | NG | ≤ 15 | 4 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0016 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Hardness | mg/L | NG | ≤ 200 | 62 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Iodide | mg/L | ≤ 0.5 | NG | 0.03 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Iron | mg/L | NG | ≤ 0.3 | 0.0026 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Lead | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Magnesium | mg/L | NG | NG | 6.93 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0140 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 15 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Nickel | mg/L | ≤ 0.02 | NG | 0.0015 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.78 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | pH | pH units | NG | 6.5 - 8.5 | 9.0 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Potassium | mg/L | NG | NG | 5.24 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Silica - reactive | mg/L | NG | ≤ 80 | 6.78 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Sodium | mg/L | NG | ≤ 180 | 42.0 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Sulphate | mg/L | NG | ≤ 250 | 53.8 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Total dissolved solids | mg/L | NG | ≤ 600 | 196 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Uranium | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Zinc | mg/L | NG | ≤ 3 | 0.0018 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Hardness - English Degrees | °e | NG | NG | 4.34 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Hardness - French Degrees | °f | NG | NG | 6.2 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Hardness - German Degrees | °dH | NG | NG | 3.47 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Loxton | Hardness - International | PPM or mg/L | NG | NG | 62 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Northern | Melrose | Alkalinity | mg/L | NG | NG | 302 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.004 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Arsenic | mg/L | ≤ 0.01 | NG | 0.00068 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Barium | mg/L | ≤ 2 | NG | 0.0956 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Bicarbonate | mg/L | NG | NG | 368 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Boron | mg/L | ≤ 4 | NG | 0.542 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Calcium | mg/L | NG | NG | 59.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chloride | mg/L | NG | ≤ 250 | 582 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Chromium | mg/L | ≤ 0.05 | NG | 0.0025 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0185 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Fluoride | mg/L | ≤ 1.5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Hardness | mg/L | NG | ≤ 200 | 346 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Iodide | mg/L | ≤ 0.5 | NG | 0.04 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Iron | mg/L | NG | ≤ 0.3 | 0.0050 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Magnesium | mg/L | NG | NG | 48.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 2.45 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Potassium | mg/L | NG | NG | 7.83 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Selenium | mg/L | ≤ 0.01 | NG | 0.0029 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Silica - reactive | mg/L | NG | ≤ 80 | 14.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Sodium | mg/L | NG | ≤ 180 | 401 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Sulphate | mg/L | NG | ≤ 250 | 161.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Total dissolved solids | mg/L | NG | ≤ 600 | 1,498 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Uranium | mg/L | ≤ 0.02 | NG | 0.0035 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Zinc | mg/L | NG | ≤ 3 | 0.0112 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Hardness - English Degrees | °e | NG | NG | 24.22 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Hardness - French Degrees | °f | NG | NG | 34.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Hardness - German Degrees | °dH | NG | NG | 19.38 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Melrose | Hardness - International | PPM or mg/L | NG | NG | 346 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Alkalinity | mg/L | NG | NG | 85 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.012 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Arsenic | mg/L | ≤ 0.01 | NG | 0.00050 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Barium | mg/L | ≤ 2 | NG | 0.0498 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Bicarbonate | mg/L | NG | NG | 104 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Boron | mg/L | ≤ 4 | NG | 0.031 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Calcium | mg/L | NG | NG | 17.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chloral hydrate | µg/L | ≤ 100 | NG | 6.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chloride | mg/L | NG | ≤ 250 | 50 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0063 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Dichloroacetic acid | µg/L | ≤ 100 | NG | 8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Hardness | mg/L | NG | ≤ 200 | 77 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Iron | mg/L | NG | ≤ 0.3 | 0.0057 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Magnesium | mg/L | NG | NG | 7.94 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0020 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.79 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | pH | pH units | NG | 6.5 - 8.5 | 7.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Potassium | mg/L | NG | NG | 6.71 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Silica - reactive | mg/L | NG | ≤ 80 | 0.74 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Sodium | mg/L | NG | ≤ 180 | 35.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Sulphate | mg/L | NG | ≤ 250 | 6.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Total dissolved solids | mg/L | NG | ≤ 600 | 198 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Trichloroacetic acid | µg/L | ≤ 100 | NG | 12 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 113 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Turbidity | NTU | NG | ≤ 5 | 0.22 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Zinc | mg/L | NG | ≤ 3 | 0.0053 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Hardness - English Degrees | °e | NG | NG | 5.39 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Hardness - French Degrees | °f | NG | NG | 7.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Hardness - German Degrees | °dH | NG | NG | 4.31 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Moorook | Hardness - International | PPM or mg/L | NG | NG | 77 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Alkalinity | mg/L | NG | NG | 74 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.021 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.23 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Arsenic | mg/L | ≤ 0.01 | NG | 0.00046 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Barium | mg/L | ≤ 2 | NG | 0.0470 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Bicarbonate | mg/L | NG | NG | 74 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Boron | mg/L | ≤ 4 | NG | 0.027 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Calcium | mg/L | NG | NG | 16.0 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Carbonate | mg/L | NG | NG | 8 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Chloride | mg/L | NG | ≤ 250 | 40 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Colour | HU | NG | ≤ 15 | 2 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0059 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Hardness | mg/L | NG | ≤ 200 | 71 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Iron | mg/L | NG | ≤ 0.3 | 0.0041 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Magnesium | mg/L | NG | NG | 7.52 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0026 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Mercury | mg/L | ≤ 0.001 | NG | 0.00003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 5 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.17 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | pH | pH units | NG | 6.5 - 8.5 | 8.8 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Potassium | mg/L | NG | NG | 5.73 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Silica - reactive | mg/L | NG | ≤ 80 | 4.85 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Sodium | mg/L | NG | ≤ 180 | 49.4 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Sulphate | mg/L | NG | ≤ 250 | 60.1 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Total dissolved solids | mg/L | NG | ≤ 600 | 231 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Turbidity | NTU | NG | ≤ 5 | 0.10 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Zinc | mg/L | NG | ≤ 3 | 0.0026 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Hardness - English Degrees | °e | NG | NG | 4.97 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Hardness - French Degrees | °f | NG | NG | 7.1 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Hardness - German Degrees | °dH | NG | NG | 3.98 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Northern | Hardness - International | PPM or mg/L | NG | NG | 71 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Alkalinity | mg/L | NG | NG | 75 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.016 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.20 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Arsenic | mg/L | ≤ 0.01 | NG | 0.00049 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Barium | mg/L | ≤ 2 | NG | 0.0438 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Bicarbonate | mg/L | NG | NG | 79 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Calcium | mg/L | NG | NG | 19.0 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Carbonate | mg/L | NG | NG | 6 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Chloride | mg/L | NG | ≤ 250 | 39 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Colour | HU | NG | ≤ 15 | 2 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0056 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Hardness | mg/L | NG | ≤ 200 | 76 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Iron | mg/L | NG | ≤ 0.3 | 0.0059 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Magnesium | mg/L | NG | NG | 6.97 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0023 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 12 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.57 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | pH | pH units | NG | 6.5 - 8.5 | 8.9 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Potassium | mg/L | NG | NG | 5.88 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Silica - reactive | mg/L | NG | ≤ 80 | 5.83 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Sodium | mg/L | NG | ≤ 180 | 51.1 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Sulphate | mg/L | NG | ≤ 250 | 61.6 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Total dissolved solids | mg/L | NG | ≤ 600 | 236 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Zinc | mg/L | NG | ≤ 3 | 0.0018 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Hardness - English Degrees | °e | NG | NG | 5.32 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Hardness - French Degrees | °f | NG | NG | 7.6 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Hardness - German Degrees | °dH | NG | NG | 4.26 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Morgan/Swan Reach | Hardness - International | PPM or mg/L | NG | NG | 76 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Alkalinity | mg/L | NG | NG | 204 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.004 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Arsenic | mg/L | ≤ 0.01 | NG | 0.00038 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Barium | mg/L | ≤ 2 | NG | 0.0486 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Bicarbonate | mg/L | NG | NG | 249 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Boron | mg/L | ≤ 4 | NG | 0.294 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Calcium | mg/L | NG | NG | 59.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chloride | mg/L | NG | ≤ 250 | 292 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Chromium | mg/L | ≤ 0.05 | NG | 0.0023 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0627 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Hardness | mg/L | NG | ≤ 200 | 317 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Iodide | mg/L | ≤ 0.5 | NG | <0.02 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Iron | mg/L | NG | ≤ 0.3 | 0.0022 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Magnesium | mg/L | NG | NG | 40.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Nickel | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 5.45 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Potassium | mg/L | NG | NG | 2.98 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Selenium | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Silica - reactive | mg/L | NG | ≤ 80 | 18.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Sodium | mg/L | NG | ≤ 180 | 181 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Sulphate | mg/L | NG | ≤ 250 | 104.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Total dissolved solids | mg/L | NG | ≤ 600 | 830 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Uranium | mg/L | ≤ 0.02 | NG | 0.0021 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Zinc | mg/L | NG | ≤ 3 | 0.0090 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Hardness - English Degrees | °e | NG | NG | 22.19 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Hardness - French Degrees | °f | NG | NG | 31.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Hardness - German Degrees | °dH | NG | NG | 17.75 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Parachilna | Hardness - International | PPM or mg/L | NG | NG | 317 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Alkalinity | mg/L | NG | NG | 428 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Arsenic | mg/L | ≤ 0.01 | NG | 0.00102 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Barium | mg/L | ≤ 2 | NG | 0.0781 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Bicarbonate | mg/L | NG | NG | 522 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Boron | mg/L | ≤ 4 | NG | 0.223 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Calcium | mg/L | NG | NG | 80.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chloride | mg/L | NG | ≤ 250 | 402 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Chromium | mg/L | ≤ 0.05 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0204 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Hardness | mg/L | NG | ≤ 200 | 499 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Iron | mg/L | NG | ≤ 0.3 | 0.0099 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Magnesium | mg/L | NG | NG | 72.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Nickel | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.47 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Potassium | mg/L | NG | NG | 7.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Selenium | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Silica - reactive | mg/L | NG | ≤ 80 | 15.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Sodium | mg/L | NG | ≤ 180 | 230 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Sulphate | mg/L | NG | ≤ 250 | 87.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Total dissolved solids | mg/L | NG | ≤ 600 | 1,195 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Uranium | mg/L | ≤ 0.02 | NG | 0.0050 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Zinc | mg/L | NG | ≤ 3 | 0.0134 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Hardness - English Degrees | °e | NG | NG | 34.93 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Hardness - French Degrees | °f | NG | NG | 49.9 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Hardness - German Degrees | °dH | NG | NG | 27.94 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Quorn | Hardness - International | PPM or mg/L | NG | NG | 499 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Renmark | Alkalinity | mg/L | NG | NG | 58 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.013 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Arsenic | mg/L | ≤ 0.01 | NG | 0.00051 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Barium | mg/L | ≤ 2 | NG | 0.0477 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Bicarbonate | mg/L | NG | NG | 71 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Boron | mg/L | ≤ 4 | NG | 0.024 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Calcium | mg/L | NG | NG | 16.9 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Carbonate | mg/L | NG | NG | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chloral hydrate | µg/L | ≤ 100 | NG | 26.6 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chloride | mg/L | NG | ≤ 250 | 30 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chloroacetic acid | µg/L | ≤ 150 | NG | 5 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0202 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Dichloroacetic acid | µg/L | ≤ 100 | NG | 44 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Hardness | mg/L | NG | ≤ 200 | 71 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Iron | mg/L | NG | ≤ 0.3 | 0.0079 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Magnesium | mg/L | NG | NG | 7.10 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0042 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Nickel | mg/L | ≤ 0.02 | NG | 0.0011 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.50 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | pH | pH units | NG | 6.5 - 8.5 | 7.7 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Potassium | mg/L | NG | NG | 5.82 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Silica - reactive | mg/L | NG | ≤ 80 | 5.20 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Sodium | mg/L | NG | ≤ 180 | 36.7 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Sulphate | mg/L | NG | ≤ 250 | 53.1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Total dissolved solids | mg/L | NG | ≤ 600 | 194 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Trichloroacetic acid | µg/L | ≤ 100 | NG | 47 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 163 | 93.2% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Turbidity | NTU | NG | ≤ 5 | 0.17 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Zinc | mg/L | NG | ≤ 3 | 0.0038 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Hardness - English Degrees | °e | NG | NG | 4.97 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Hardness - French Degrees | °f | NG | NG | 7.1 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Hardness - German Degrees | °dH | NG | NG | 3.98 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Renmark | Hardness - International | PPM or mg/L | NG | NG | 71 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Alkalinity | mg/L | NG | NG | 66 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.014 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Arsenic | mg/L | ≤ 0.01 | NG | 0.00049 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Barium | mg/L | ≤ 2 | NG | 0.0572 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Bicarbonate | mg/L | NG | NG | 81 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Boron | mg/L | ≤ 4 | NG | 0.032 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Calcium | mg/L | NG | NG | 18.2 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chloral hydrate | µg/L | ≤ 100 | NG | 13.0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chloride | mg/L | NG | ≤ 250 | 44 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chloroacetic acid | µg/L | ≤ 150 | NG | 6 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0321 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Dichloroacetic acid | µg/L | ≤ 100 | NG | 22 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Hardness | mg/L | NG | ≤ 200 | 81 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Iron | mg/L | NG | ≤ 0.3 | 0.0113 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Magnesium | mg/L | NG | NG | 8.80 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0091 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0007 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Nickel | mg/L | ≤ 0.02 | NG | 0.0011 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.26 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Potassium | mg/L | NG | NG | 6.84 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Silica - reactive | mg/L | NG | ≤ 80 | 1.03 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Sodium | mg/L | NG | ≤ 180 | 45.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Sulphate | mg/L | NG | ≤ 250 | 55.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Total dissolved solids | mg/L | NG | ≤ 600 | 226 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Trichloroacetic acid | µg/L | ≤ 100 | NG | 24 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 140 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Turbidity | NTU | NG | ≤ 5 | 0.23 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Zinc | mg/L | NG | ≤ 3 | 0.0060 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Hardness - English Degrees | °e | NG | NG | 5.67 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Hardness - French Degrees | °f | NG | NG | 8.1 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Hardness - German Degrees | °dH | NG | NG | 4.54 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Waikerie | Hardness - International | PPM or mg/L | NG | NG | 81 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Northern | Wilmington | Alkalinity | mg/L | NG | NG | 93 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Arsenic | mg/L | ≤ 0.01 | NG | 0.00083 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Barium | mg/L | ≤ 2 | NG | 0.1739 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Bicarbonate | mg/L | NG | NG | 113 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Boron | mg/L | ≤ 4 | NG | 0.022 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Calcium | mg/L | NG | NG | 17.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chloride | mg/L | NG | ≤ 250 | 103 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Copper | mg/L | ≤ 2 | ≤ 1 | 0.1121 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Fluoride | mg/L | ≤ 1.5 | NG | 0.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Hardness | mg/L | NG | ≤ 200 | 117 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Iron | mg/L | NG | ≤ 0.3 | 0.0336 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Magnesium | mg/L | NG | NG | 17.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Nickel | mg/L | ≤ 0.02 | NG | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.91 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | pH | pH units | NG | 6.5 - 8.5 | 7.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Potassium | mg/L | NG | NG | 14.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Selenium | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Silica - reactive | mg/L | NG | ≤ 80 | 25.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Sodium | mg/L | NG | ≤ 180 | 53.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Sulphate | mg/L | NG | ≤ 250 | 18.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Total dissolved solids | mg/L | NG | ≤ 600 | 322 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 12 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Turbidity | NTU | NG | ≤ 5 | 0.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Zinc | mg/L | NG | ≤ 3 | 0.0136 | NA | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Hardness - English Degrees | °e | NG | NG | 8.19 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Hardness - French Degrees | °f | NG | NG | 11.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Hardness - German Degrees | °dH | NG | NG | 6.55 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Wilmington | Hardness - International | PPM or mg/L | NG | NG | 117 | NG | Chlorine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Alkalinity | mg/L | NG | NG | 83 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.007 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.39 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Arsenic | mg/L | ≤ 0.01 | NG | 0.00062 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Barium | mg/L | ≤ 2 | NG | 0.0432 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Bicarbonate | mg/L | NG | NG | 91 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Calcium | mg/L | NG | NG | 14.8 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Carbonate | mg/L | NG | NG | 5 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Chloride | mg/L | NG | ≤ 250 | 56 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.2 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.2 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Colour | HU | NG | ≤ 15 | 2 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0011 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Hardness | mg/L | NG | ≤ 200 | 68 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Iron | mg/L | NG | ≤ 0.3 | 0.0013 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Lead | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Magnesium | mg/L | NG | NG | 7.39 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0011 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | <2 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.86 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | pH | pH units | NG | 6.5 - 8.5 | 8.8 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Potassium | mg/L | NG | NG | 5.82 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Silica - reactive | mg/L | NG | ≤ 80 | 4.57 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Sodium | mg/L | NG | ≤ 180 | 39.5 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Sulphate | mg/L | NG | ≤ 250 | 7.4 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Total dissolved solids | mg/L | NG | ≤ 600 | 201 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Zinc | mg/L | NG | ≤ 3 | 0.0006 | NA | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Hardness - English Degrees | °e | NG | NG | 4.76 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Hardness - French Degrees | °f | NG | NG | 6.8 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Hardness - German Degrees | °dH | NG | NG | 3.81 | NG | Chloramine | 01/04/2022 - 31/03/2023
Northern | Woolpunda | Hardness - International | PPM or mg/L | NG | NG | 68 | NG | Chloramine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Alkalinity | mg/L | NG | NG | 52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.018 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Arsenic | mg/L | ≤ 0.01 | NG | 0.00036 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Barium | mg/L | ≤ 2 | NG | 0.0331 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Bicarbonate | mg/L | NG | NG | 64 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Boron | mg/L | ≤ 4 | NG | 0.027 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Calcium | mg/L | NG | NG | 20.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chloral hydrate | µg/L | ≤ 100 | NG | 16.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chloride | mg/L | NG | ≤ 250 | 105 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0172 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Dichloroacetic acid | µg/L | ≤ 100 | NG | 10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Fluoride | mg/L | ≤ 1.5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Hardness | mg/L | NG | ≤ 200 | 103 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Iron | mg/L | NG | ≤ 0.3 | 0.0243 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Magnesium | mg/L | NG | NG | 12.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0015 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.21 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Potassium | mg/L | NG | NG | 3.83 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Silica - reactive | mg/L | NG | ≤ 80 | 3.32 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Sodium | mg/L | NG | ≤ 180 | 57.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Sulphate | mg/L | NG | ≤ 250 | 33.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Total dissolved solids | mg/L | NG | ≤ 600 | 297 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Trichloroacetic acid | µg/L | ≤ 100 | NG | 16 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 174 | 99.1% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Turbidity | NTU | NG | ≤ 5 | 0.19 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Zinc | mg/L | NG | ≤ 3 | 0.0028 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Hardness - English Degrees | °e | NG | NG | 7.21 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Hardness - French Degrees | °f | NG | NG | 10.3 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Hardness - German Degrees | °dH | NG | NG | 5.77 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Barossa | Hardness - International | PPM or mg/L | NG | NG | 103 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Alkalinity | mg/L | NG | NG | 85 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.008 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Arsenic | mg/L | ≤ 0.01 | NG | 0.00035 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Barium | mg/L | ≤ 2 | NG | 0.0388 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Bicarbonate | mg/L | NG | NG | 104 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Boron | mg/L | ≤ 4 | NG | 0.021 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Calcium | mg/L | NG | NG | 15.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chloral hydrate | µg/L | ≤ 100 | NG | 21.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chloride | mg/L | NG | ≤ 250 | 44 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0391 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Dichloroacetic acid | µg/L | ≤ 100 | NG | 44 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Hardness | mg/L | NG | ≤ 200 | 66 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Iron | mg/L | NG | ≤ 0.3 | 0.0049 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Magnesium | mg/L | NG | NG | 6.62 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.46 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Potassium | mg/L | NG | NG | 5.31 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Silica - reactive | mg/L | NG | ≤ 80 | 5.50 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Sodium | mg/L | NG | ≤ 180 | 32.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Sulphate | mg/L | NG | ≤ 250 | 5.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Total dissolved solids | mg/L | NG | ≤ 600 | 177 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Trichloroacetic acid | µg/L | ≤ 100 | NG | 39 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 145 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Uranium | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Zinc | mg/L | NG | ≤ 3 | 0.0023 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Hardness - English Degrees | °e | NG | NG | 4.62 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Hardness - French Degrees | °f | NG | NG | 6.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Hardness - German Degrees | °dH | NG | NG | 3.70 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Cowirra | Hardness - International | PPM or mg/L | NG | NG | 66 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Happy Valley | Alkalinity | mg/L | NG | NG | 61 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.023 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Arsenic | mg/L | ≤ 0.01 | NG | 0.00035 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Barium | mg/L | ≤ 2 | NG | 0.0282 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Bicarbonate | mg/L | NG | NG | 74 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Boron | mg/L | ≤ 4 | NG | 0.043 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Calcium | mg/L | NG | NG | 26.3 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chloral hydrate | µg/L | ≤ 100 | NG | 21.9 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chloride | mg/L | NG | ≤ 250 | 79 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0152 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Dichloroacetic acid | µg/L | ≤ 100 | NG | 20 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Hardness | mg/L | NG | ≤ 200 | 116 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Iron | mg/L | NG | ≤ 0.3 | 0.0097 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Magnesium | mg/L | NG | NG | 12.2 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.064 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Potassium | mg/L | NG | NG | 4.91 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Silica - reactive | mg/L | NG | ≤ 80 | 1.79 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Sodium | mg/L | NG | ≤ 180 | 44.6 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Sulphate | mg/L | NG | ≤ 250 | 43.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Total dissolved solids | mg/L | NG | ≤ 600 | 275 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Trichloroacetic acid | µg/L | ≤ 100 | NG | 18 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 228 | 75.0% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Zinc | mg/L | NG | ≤ 3 | 0.0039 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Hardness - English Degrees | °e | NG | NG | 8.12 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Hardness - French Degrees | °f | NG | NG | 11.6 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Hardness - German Degrees | °dH | NG | NG | 6.50 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Happy Valley | Hardness - International | PPM or mg/L | NG | NG | 116 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023 | Can be supplied by Adelaide Desalination Plant and other Metropolitan water treatment plants.
Outer Metro | Hawker | Alkalinity | mg/L | NG | NG | 77 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.005 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Barium | mg/L | ≤ 2 | NG | 0.0026 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Bicarbonate | mg/L | NG | NG | 94 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Boron | mg/L | ≤ 4 | NG | 0.290 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Calcium | mg/L | NG | NG | 16.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chloride | mg/L | NG | ≤ 250 | 103 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0021 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Hardness | mg/L | NG | ≤ 200 | 102 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Iron | mg/L | NG | ≤ 0.3 | 0.0016 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Magnesium | mg/L | NG | NG | 14.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Nickel | mg/L | ≤ 0.02 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | <0.014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | pH | pH units | NG | 6.5 - 8.5 | 8.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Potassium | mg/L | NG | NG | 1.78 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Silica - reactive | mg/L | NG | ≤ 80 | 1.97 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Sodium | mg/L | NG | ≤ 180 | 74.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Sulphate | mg/L | NG | ≤ 250 | 48.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Total dissolved solids | mg/L | NG | ≤ 600 | 327 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Uranium | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Zinc | mg/L | NG | ≤ 3 | 0.0041 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Hardness - English Degrees | °e | NG | NG | 7.14 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Hardness - French Degrees | °f | NG | NG | 10.2 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Hardness - German Degrees | °dH | NG | NG | 5.71 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Hawker | Hardness - International | PPM or mg/L | NG | NG | 102 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Alkalinity | mg/L | NG | NG | 89 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.011 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Arsenic | mg/L | ≤ 0.01 | NG | 0.00045 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Barium | mg/L | ≤ 2 | NG | 0.0453 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Bicarbonate | mg/L | NG | NG | 108 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Boron | mg/L | ≤ 4 | NG | 0.022 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Calcium | mg/L | NG | NG | 17.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chloral hydrate | µg/L | ≤ 100 | NG | 15.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chloride | mg/L | NG | ≤ 250 | 57 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0246 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Dichloroacetic acid | µg/L | ≤ 100 | NG | 32 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Hardness | mg/L | NG | ≤ 200 | 79 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Iron | mg/L | NG | ≤ 0.3 | 0.0006 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Magnesium | mg/L | NG | NG | 8.42 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Mercury | mg/L | ≤ 0.001 | NG | 0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.59 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Potassium | mg/L | NG | NG | 6.24 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Silica - reactive | mg/L | NG | ≤ 80 | 4.25 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Sodium | mg/L | NG | ≤ 180 | 39.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Sulphate | mg/L | NG | ≤ 250 | 8.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Total dissolved solids | mg/L | NG | ≤ 600 | 206 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Trichloroacetic acid | µg/L | ≤ 100 | NG | 28 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 130 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Zinc | mg/L | NG | ≤ 3 | 0.0020 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Hardness - English Degrees | °e | NG | NG | 5.53 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Hardness - French Degrees | °f | NG | NG | 7.9 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Hardness - German Degrees | °dH | NG | NG | 4.42 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Kanmantoo | Hardness - International | PPM or mg/L | NG | NG | 79 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Alkalinity | mg/L | NG | NG | 60 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.012 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Arsenic | mg/L | ≤ 0.01 | NG | 0.00051 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Barium | mg/L | ≤ 2 | NG | 0.0574 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Bicarbonate | mg/L | NG | NG | 73 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Boron | mg/L | ≤ 4 | NG | 0.031 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Calcium | mg/L | NG | NG | 17.0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chloral hydrate | µg/L | ≤ 100 | NG | 13.5 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chloride | mg/L | NG | ≤ 250 | 46 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0254 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Dichloroacetic acid | µg/L | ≤ 100 | NG | 23 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Hardness | mg/L | NG | ≤ 200 | 79 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Iron | mg/L | NG | ≤ 0.3 | 0.0212 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Magnesium | mg/L | NG | NG | 8.97 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0202 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Mercury | mg/L | ≤ 0.001 | NG | 0.00005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Nickel | mg/L | ≤ 0.02 | NG | 0.0012 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.18 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Potassium | mg/L | NG | NG | 6.18 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Silica - reactive | mg/L | NG | ≤ 80 | 4.77 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Sodium | mg/L | NG | ≤ 180 | 44.7 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Sulphate | mg/L | NG | ≤ 250 | 56.3 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Total dissolved solids | mg/L | NG | ≤ 600 | 233 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Trichloroacetic acid | µg/L | ≤ 100 | NG | 32 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 132 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Turbidity | NTU | NG | ≤ 5 | 0.19 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Zinc | mg/L | NG | ≤ 3 | 0.0046 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Hardness - English Degrees | °e | NG | NG | 5.53 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Hardness - French Degrees | °f | NG | NG | 7.9 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Hardness - German Degrees | °dH | NG | NG | 4.42 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mannum | Hardness - International | PPM or mg/L | NG | NG | 79 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Alkalinity | mg/L | NG | NG | 24 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.030 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Barium | mg/L | ≤ 2 | NG | 0.0142 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Bicarbonate | mg/L | NG | NG | 29 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Boron | mg/L | ≤ 4 | NG | 0.032 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Calcium | mg/L | NG | NG | 10.70 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chloral hydrate | µg/L | ≤ 100 | NG | 3.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chloride | mg/L | NG | ≤ 250 | 244 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.9 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0106 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Dichloroacetic acid | µg/L | ≤ 100 | NG | 5 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Hardness | mg/L | NG | ≤ 200 | 84 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Iodide | mg/L | ≤ 0.5 | NG | <0.02 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Iron | mg/L | NG | ≤ 0.3 | 0.0139 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Magnesium | mg/L | NG | NG | 13.78 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0010 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.69 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Potassium | mg/L | NG | NG | 2.70 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Silica - reactive | mg/L | NG | ≤ 80 | 3.92 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Sodium | mg/L | NG | ≤ 180 | 156 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Sulphate | mg/L | NG | ≤ 250 | 60.2 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Total dissolved solids | mg/L | NG | ≤ 600 | 558 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Trichloroacetic acid | µg/L | ≤ 100 | NG | 2 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 128 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Uranium | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Zinc | mg/L | NG | ≤ 3 | 0.0067 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Hardness - English Degrees | °e | NG | NG | 5.88 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Hardness - French Degrees | °f | NG | NG | 8.4 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Hardness - German Degrees | °dH | NG | NG | 4.70 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Middle River | Hardness - International | PPM or mg/L | NG | NG | 84 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Alkalinity | mg/L | NG | NG | 124 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Barium | mg/L | ≤ 2 | NG | 0.0152 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Bicarbonate | mg/L | NG | NG | 151 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Calcium | mg/L | NG | NG | 12.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chloride | mg/L | NG | ≤ 250 | 60 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0037 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Fluoride | mg/L | ≤ 1.5 | NG | 0.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Hardness | mg/L | NG | ≤ 200 | 55 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Iron | mg/L | NG | ≤ 0.3 | 0.0024 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Magnesium | mg/L | NG | NG | 6.03 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.32 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Potassium | mg/L | NG | NG | 2.47 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Silica - reactive | mg/L | NG | ≤ 80 | 18.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Sodium | mg/L | NG | ≤ 180 | 67.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Sulphate | mg/L | NG | ≤ 250 | 8.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Total dissolved solids | mg/L | NG | ≤ 600 | 245 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | <4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Turbidity | NTU | NG | ≤ 5 | 0.14 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Uranium | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Zinc | mg/L | NG | ≤ 3 | 0.0051 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Hardness - English Degrees | °e | NG | NG | 3.85 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Hardness - French Degrees | °f | NG | NG | 5.5 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Hardness - German Degrees | °dH | NG | NG | 3.08 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Compass | Hardness - International | PPM or mg/L | NG | NG | 55 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Alkalinity | mg/L | NG | NG | 66 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.007 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Arsenic | mg/L | ≤ 0.01 | NG | 0.00061 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Barium | mg/L | ≤ 2 | NG | 0.0403 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Bicarbonate | mg/L | NG | NG | 80 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Boron | mg/L | ≤ 4 | NG | 0.022 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Calcium | mg/L | NG | NG | 14.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chloral hydrate | µg/L | ≤ 100 | NG | 23.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chloride | mg/L | NG | ≤ 250 | 37 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chloroacetic acid | µg/L | ≤ 150 | NG | 3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0276 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Dichloroacetic acid | µg/L | ≤ 100 | NG | 51 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Fluoride | mg/L | ≤ 1.5 | NG | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Hardness | mg/L | NG | ≤ 200 | 66 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Iron | mg/L | NG | ≤ 0.3 | 0.0028 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Magnesium | mg/L | NG | NG | 7.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0015 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Nickel | mg/L | ≤ 0.02 | NG | 0.0010 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.30 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Potassium | mg/L | NG | NG | 5.56 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Silica - reactive | mg/L | NG | ≤ 80 | 5.69 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Sodium | mg/L | NG | ≤ 180 | 28.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Sulphate | mg/L | NG | ≤ 250 | 12.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Total dissolved solids | mg/L | NG | ≤ 600 | 160 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Trichloroacetic acid | µg/L | ≤ 100 | NG | 83 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 181 | 88.9% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Zinc | mg/L | NG | ≤ 3 | 0.0033 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Hardness - English Degrees | °e | NG | NG | 4.62 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Hardness - French Degrees | °f | NG | NG | 6.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Hardness - German Degrees | °dH | NG | NG | 3.70 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mt Pleasant | Hardness - International | PPM or mg/L | NG | NG | 66 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Alkalinity | mg/L | NG | NG | 64 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.025 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Arsenic | mg/L | ≤ 0.01 | NG | 0.00046 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Barium | mg/L | ≤ 2 | NG | 0.0486 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Bicarbonate | mg/L | NG | NG | 79 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Boron | mg/L | ≤ 4 | NG | 0.031 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Calcium | mg/L | NG | NG | 21.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chloral hydrate | µg/L | ≤ 100 | NG | 24.2 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chloride | mg/L | NG | ≤ 250 | 43 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.9 | 99.5% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.0 | 99.5% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0227 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Dichloroacetic acid | µg/L | ≤ 100 | NG | 50 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Hardness | mg/L | NG | ≤ 200 | 87 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Iron | mg/L | NG | ≤ 0.3 | 0.0179 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Magnesium | mg/L | NG | NG | 8.00 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0064 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Nickel | mg/L | ≤ 0.02 | NG | 0.0011 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.53 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Potassium | mg/L | NG | NG | 5.99 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Silica - reactive | mg/L | NG | ≤ 80 | 3.89 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Sodium | mg/L | NG | ≤ 180 | 38.1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Sulphate | mg/L | NG | ≤ 250 | 54.4 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Total dissolved solids | mg/L | NG | ≤ 600 | 217 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Trichloroacetic acid | µg/L | ≤ 100 | NG | 58 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 192 | 72.7% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Turbidity | NTU | NG | ≤ 5 | 0.13 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Zinc | mg/L | NG | ≤ 3 | 0.0057 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Hardness - English Degrees | °e | NG | NG | 6.09 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Hardness - French Degrees | °f | NG | NG | 8.7 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Hardness - German Degrees | °dH | NG | NG | 4.87 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Murray Bridge | Hardness - International | PPM or mg/L | NG | NG | 87 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Alkalinity | mg/L | NG | NG | 78 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.015 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Arsenic | mg/L | ≤ 0.01 | NG | 0.00047 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Barium | mg/L | ≤ 2 | NG | 0.0395 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Bicarbonate | mg/L | NG | NG | 95 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Boron | mg/L | ≤ 4 | NG | 0.029 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Calcium | mg/L | NG | NG | 15.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chloral hydrate | µg/L | ≤ 100 | NG | 6.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chloride | mg/L | NG | ≤ 250 | 45 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Colour | HU | NG | ≤ 15 | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0470 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Dichloroacetic acid | µg/L | ≤ 100 | NG | 12 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Hardness | mg/L | NG | ≤ 200 | 67 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Iron | mg/L | NG | ≤ 0.3 | 0.0129 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Magnesium | mg/L | NG | NG | 7.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.48 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Potassium | mg/L | NG | NG | 5.68 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Silica - reactive | mg/L | NG | ≤ 80 | 0.82 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Sodium | mg/L | NG | ≤ 180 | 31.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Sulphate | mg/L | NG | ≤ 250 | 6.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Total dissolved solids | mg/L | NG | ≤ 600 | 176 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Trichloroacetic acid | µg/L | ≤ 100 | NG | 27 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 188 | 66.7% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Turbidity | NTU | NG | ≤ 5 | 0.12 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Zinc | mg/L | NG | ≤ 3 | 0.0080 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Hardness - English Degrees | °e | NG | NG | 4.69 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Hardness - French Degrees | °f | NG | NG | 6.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Hardness - German Degrees | °dH | NG | NG | 3.75 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Mypolonga | Hardness - International | PPM or mg/L | NG | NG | 67 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Alkalinity | mg/L | NG | NG | 76 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.055 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.28 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Arsenic | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Barium | mg/L | ≤ 2 | NG | 0.0233 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Bicarbonate | mg/L | NG | NG | 83 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Boron | mg/L | ≤ 4 | NG | 0.035 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Calcium | mg/L | NG | NG | 26.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Carbonate | mg/L | NG | NG | 5 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Chloride | mg/L | NG | ≤ 250 | 152 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Colour | HU | NG | ≤ 15 | 3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0149 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Fluoride | mg/L | ≤ 1.5 | NG | 0.73 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Hardness | mg/L | NG | ≤ 200 | 129 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Iron | mg/L | NG | ≤ 0.3 | 0.0075 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Magnesium | mg/L | NG | NG | 15.1 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0043 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Mercury | mg/L | ≤ 0.001 | NG | 0.00010 | 94.7% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.48 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | pH | pH units | NG | 6.5 - 8.5 | 8.7 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Potassium | mg/L | NG | NG | 6.85 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Silica - reactive | mg/L | NG | ≤ 80 | 2.14 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Sodium | mg/L | NG | ≤ 180 | 102 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Sulphate | mg/L | NG | ≤ 250 | 64.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Total dissolved solids | mg/L | NG | ≤ 600 | 451 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 109 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Zinc | mg/L | NG | ≤ 3 | 0.0017 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Hardness - English Degrees | °e | NG | NG | 9.02 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Hardness - French Degrees | °f | NG | NG | 12.9 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Hardness - German Degrees | °dH | NG | NG | 7.25 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga (supplying Victor Harbor and the Fleurieu) | Hardness - International | PPM or mg/L | NG | NG | 129 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Alkalinity | mg/L | NG | NG | 76 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.055 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.28 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Arsenic | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Barium | mg/L | ≤ 2 | NG | 0.0233 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Bicarbonate | mg/L | NG | NG | 83 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Boron | mg/L | ≤ 4 | NG | 0.035 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Calcium | mg/L | NG | NG | 26.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Carbonate | mg/L | NG | NG | 5 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Chloride | mg/L | NG | ≤ 250 | 152 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Colour | HU | NG | ≤ 15 | 3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0149 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Fluoride | mg/L | ≤ 1.5 | NG | 0.73 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Hardness | mg/L | NG | ≤ 200 | 129 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Iron | mg/L | NG | ≤ 0.3 | 0.0075 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Magnesium | mg/L | NG | NG | 15.1 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0043 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Mercury | mg/L | ≤ 0.001 | NG | 0.00010 | 94.7% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Nickel | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.48 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | pH | pH units | NG | 6.5 - 8.5 | 8.7 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Potassium | mg/L | NG | NG | 6.85 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Silica - reactive | mg/L | NG | ≤ 80 | 2.14 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Sodium | mg/L | NG | ≤ 180 | 102 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Sulphate | mg/L | NG | ≤ 250 | 64.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Total dissolved solids | mg/L | NG | ≤ 600 | 451 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 109 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Zinc | mg/L | NG | ≤ 3 | 0.0017 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Hardness - English Degrees | °e | NG | NG | 9.02 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Hardness - French Degrees | °f | NG | NG | 12.9 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Hardness - German Degrees | °dH | NG | NG | 7.25 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Myponga, Yankalilla, Normanville and Carrickalinga | Hardness - International | PPM or mg/L | NG | NG | 129 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Alkalinity | mg/L | NG | NG | 96 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.015 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Arsenic | mg/L | ≤ 0.01 | NG | 0.00054 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Barium | mg/L | ≤ 2 | NG | 0.0461 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Bicarbonate | mg/L | NG | NG | 117 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Boron | mg/L | ≤ 4 | NG | 0.029 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Calcium | mg/L | NG | NG | 21.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chloral hydrate | µg/L | ≤ 100 | NG | 24.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chloride | mg/L | NG | ≤ 250 | 58 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0162 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Dichloroacetic acid | µg/L | ≤ 100 | NG | 24 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Hardness | mg/L | NG | ≤ 200 | 85 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Iron | mg/L | NG | ≤ 0.3 | 0.0041 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Magnesium | mg/L | NG | NG | 7.70 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.75 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Potassium | mg/L | NG | NG | 6.49 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Silica - reactive | mg/L | NG | ≤ 80 | 3.91 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Sodium | mg/L | NG | ≤ 180 | 41.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Sulphate | mg/L | NG | ≤ 250 | 7.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Total dissolved solids | mg/L | NG | ≤ 600 | 221 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Trichloroacetic acid | µg/L | ≤ 100 | NG | 59 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 155 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Zinc | mg/L | NG | ≤ 3 | 0.0018 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Hardness - English Degrees | °e | NG | NG | 5.95 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Hardness - French Degrees | °f | NG | NG | 8.5 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Hardness - German Degrees | °dH | NG | NG | 4.76 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Palmer | Hardness - International | PPM or mg/L | NG | NG | 85 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Alkalinity | mg/L | NG | NG | 78 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Barium | mg/L | ≤ 2 | NG | <0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Bicarbonate | mg/L | NG | NG | 95 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Boron | mg/L | ≤ 4 | NG | 0.650 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Calcium | mg/L | NG | NG | 28.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chloride | mg/L | NG | ≤ 250 | 130 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Colour | HU | NG | ≤ 15 | 2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0101 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Hardness | mg/L | NG | ≤ 200 | 87 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Iron | mg/L | NG | ≤ 0.3 | < 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Lead | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Magnesium | mg/L | NG | NG | 3.64 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.064 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Potassium | mg/L | NG | NG | 3.71 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Silica - reactive | mg/L | NG | ≤ 80 | <0.05 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Sodium | mg/L | NG | ≤ 180 | 78.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Sulphate | mg/L | NG | ≤ 250 | 6.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Total dissolved solids | mg/L | NG | ≤ 600 | 333 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | <4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Zinc | mg/L | NG | ≤ 3 | 0.0029 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Hardness - English Degrees | °e | NG | NG | 6.09 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Hardness - French Degrees | °f | NG | NG | 8.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Hardness - German Degrees | °dH | NG | NG | 4.87 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Penneshaw | Hardness - International | PPM or mg/L | NG | NG | 87 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Alkalinity | mg/L | NG | NG | 65 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.017 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.29 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Arsenic | mg/L | ≤ 0.01 | NG | 0.00032 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Barium | mg/L | ≤ 2 | NG | 0.0432 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Bicarbonate | mg/L | NG | NG | 67 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Boron | mg/L | ≤ 4 | NG | 0.022 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Calcium | mg/L | NG | NG | 15.2 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Carbonate | mg/L | NG | NG | 6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Chloride | mg/L | NG | ≤ 250 | 33 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 3.2 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Chlorine (total residual) | mg/L | ≤ 5 | NG | 3.2 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Colour | HU | NG | ≤ 15 | 3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0095 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | E. coli | per cent compliance | 0 | NG | 99.7% | 99.7% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Hardness | mg/L | NG | ≤ 200 | 67 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Iron | mg/L | NG | ≤ 0.3 | 0.0043 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Magnesium | mg/L | NG | NG | 7.06 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0059 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 15 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Nickel | mg/L | ≤ 0.02 | NG | 0.0010 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.86 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | pH | pH units | NG | 6.5 - 8.5 | 8.8 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Potassium | mg/L | NG | NG | 5.28 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Silica - reactive | mg/L | NG | ≤ 80 | 5.07 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Sodium | mg/L | NG | ≤ 180 | 39.4 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Sulphate | mg/L | NG | ≤ 250 | 54.5 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Total dissolved solids | mg/L | NG | ≤ 600 | 198 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Zinc | mg/L | NG | ≤ 3 | 0.0028 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Hardness - English Degrees | °e | NG | NG | 4.69 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Hardness - French Degrees | °f | NG | NG | 6.7 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Hardness - German Degrees | °dH | NG | NG | 3.75 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Summit | Hardness - International | PPM or mg/L | NG | NG | 67 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Alkalinity | mg/L | NG | NG | 74 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.019 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.28 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Arsenic | mg/L | ≤ 0.01 | NG | 0.00043 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Barium | mg/L | ≤ 2 | NG | 0.0485 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Bicarbonate | mg/L | NG | NG | 85 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Calcium | mg/L | NG | NG | 21.4 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Carbonate | mg/L | NG | NG | 2 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chloride | mg/L | NG | ≤ 250 | 38 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Colour | HU | NG | ≤ 15 | 2 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0071 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Fluoride | mg/L | ≤ 1.5 | NG | 0.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Hardness | mg/L | NG | ≤ 200 | 86 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Iodide | mg/L | ≤ 0.5 | NG | 0.03 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Iron | mg/L | NG | ≤ 0.3 | 0.0026 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Magnesium | mg/L | NG | NG | 7.84 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0045 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 23 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Nickel | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.20 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | pH | pH units | NG | 6.5 - 8.5 | 8.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Potassium | mg/L | NG | NG | 5.90 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Silica - reactive | mg/L | NG | ≤ 80 | 3.55 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Sodium | mg/L | NG | ≤ 180 | 41.8 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Sulphate | mg/L | NG | ≤ 250 | 59.5 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Total dissolved solids | mg/L | NG | ≤ 600 | 223 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Zinc | mg/L | NG | ≤ 3 | 0.0047 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Hardness - English Degrees | °e | NG | NG | 6.02 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Hardness - French Degrees | °f | NG | NG | 8.6 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Hardness - German Degrees | °dH | NG | NG | 4.82 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach | Hardness - International | PPM or mg/L | NG | NG | 86 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Alkalinity | mg/L | NG | NG | 75 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.011 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Arsenic | mg/L | ≤ 0.01 | NG | 0.00037 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Barium | mg/L | ≤ 2 | NG | 0.0413 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Bicarbonate | mg/L | NG | NG | 91 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Calcium | mg/L | NG | NG | 15.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chloral hydrate | µg/L | ≤ 100 | NG | 17.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chloride | mg/L | NG | ≤ 250 | 44 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chloroacetic acid | µg/L | ≤ 150 | NG | 3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0304 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Dichloroacetic acid | µg/L | ≤ 100 | NG | 32 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Hardness | mg/L | NG | ≤ 200 | 68 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Iron | mg/L | NG | ≤ 0.3 | 0.0113 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Magnesium | mg/L | NG | NG | 7.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.58 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Potassium | mg/L | NG | NG | 5.52 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Silica - reactive | mg/L | NG | ≤ 80 | 3.61 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Sodium | mg/L | NG | ≤ 180 | 30.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Sulphate | mg/L | NG | ≤ 250 | 5.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Total dissolved solids | mg/L | NG | ≤ 600 | 168 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Trichloroacetic acid | µg/L | ≤ 100 | NG | 26 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 125 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Turbidity | NTU | NG | ≤ 5 | 0.16 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Zinc | mg/L | NG | ≤ 3 | 0.0077 | NA | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Hardness - English Degrees | °e | NG | NG | 4.76 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Hardness - French Degrees | °f | NG | NG | 6.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Hardness - German Degrees | °dH | NG | NG | 3.81 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Swan Reach Town | Hardness - International | PPM or mg/L | NG | NG | 68 | NG | Chlorine | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Alkalinity | mg/L | NG | NG | 60 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.028 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Barium | mg/L | ≤ 2 | NG | 0.0346 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Bicarbonate | mg/L | NG | NG | 73 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Boron | mg/L | ≤ 4 | NG | 0.067 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Calcium | mg/L | NG | NG | 25.5 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chloral hydrate | µg/L | ≤ 100 | NG | 8.5 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chloride | mg/L | NG | ≤ 250 | 351 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.4 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0383 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Dichloroacetic acid | µg/L | ≤ 100 | NG | 11 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Fluoride | mg/L | ≤ 1.5 | NG | 0.11 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Hardness | mg/L | NG | ≤ 200 | 155 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Iron | mg/L | NG | ≤ 0.3 | 0.0118 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Magnesium | mg/L | NG | NG | 22.1 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0088 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Nickel | mg/L | ≤ 0.02 | NG | 0.0008 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.72 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Potassium | mg/L | NG | NG | 5.95 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Selenium | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Silica - reactive | mg/L | NG | ≤ 80 | 7.48 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Sodium | mg/L | NG | ≤ 180 | 209 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Sulphate | mg/L | NG | ≤ 250 | 107.6 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Total dissolved solids | mg/L | NG | ≤ 600 | 805 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Trichloroacetic acid | µg/L | ≤ 100 | NG | 7 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 192 | 91.7% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Turbidity | NTU | NG | ≤ 5 | 0.17 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Zinc | mg/L | NG | ≤ 3 | 0.0214 | NA | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Hardness - English Degrees | °e | NG | NG | 10.85 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Hardness - French Degrees | °f | NG | NG | 15.5 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Hardness - German Degrees | °dH | NG | NG | 8.68 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Outer Metro | Wirrina Cove | Hardness - International | PPM or mg/L | NG | NG | 155 | NG | Chlorine / UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Alkalinity | mg/L | NG | NG | 354 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.004 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Barium | mg/L | ≤ 2 | NG | 0.0449 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Bicarbonate | mg/L | NG | NG | 432 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Boron | mg/L | ≤ 4 | NG | 0.103 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Calcium | mg/L | NG | NG | 76.2 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Chloride | mg/L | NG | ≤ 250 | 173 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0063 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Fluoride | mg/L | ≤ 1.5 | NG | 0.9 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Hardness | mg/L | NG | ≤ 200 | 410 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Iodide | mg/L | ≤ 0.5 | NG | 0.02 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Iron | mg/L | NG | ≤ 0.3 | 0.0024 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Lead | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Magnesium | mg/L | NG | NG | 53.4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0015 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 15.95 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | pH | pH units | NG | 6.5 - 8.5 | 8.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Potassium | mg/L | NG | NG | 1.65 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Selenium | mg/L | ≤ 0.01 | NG | 0.0019 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Silica - reactive | mg/L | NG | ≤ 80 | 67.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Sodium | mg/L | NG | ≤ 180 | 134 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Sulphate | mg/L | NG | ≤ 250 | 93.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Total dissolved solids | mg/L | NG | ≤ 600 | 739 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Uranium | mg/L | ≤ 0.02 | NG | 0.0010 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Zinc | mg/L | NG | ≤ 3 | 0.0087 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Hardness - English Degrees | °e | NG | NG | 28.70 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Hardness - French Degrees | °f | NG | NG | 41.0 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Hardness - German Degrees | °dH | NG | NG | 22.96 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Amata | Hardness - International | PPM or mg/L | NG | NG | 410 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Davenport | Alkalinity | mg/L | NG | NG | 51 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Bicarbonate | mg/L | NG | NG | 58 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Calcium | mg/L | NG | NG | 12.3 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Carbonate | mg/L | NG | NG | 2 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 1.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.7 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 2.45 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | pH | pH units | NG | 6.5 - 8.5 | 8.6 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Total dissolved solids | mg/L | NG | ≤ 600 | 185 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Turbidity | NTU | NG | ≤ 5 | 0.21 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Hardness - English Degrees | °e | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Hardness - French Degrees | °f | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Hardness - German Degrees | °dH | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Davenport | Hardness - International | PPM or mg/L | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan Whyalla system, for more data search Morgan/Northern
Remote Communities | Gerard | Alkalinity | mg/L | NG | NG | 82 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.014 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Arsenic | mg/L | ≤ 0.01 | NG | 0.00081 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Barium | mg/L | ≤ 2 | NG | 0.0588 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Bicarbonate | mg/L | NG | NG | 100 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Boron | mg/L | ≤ 4 | NG | 0.040 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Calcium | mg/L | NG | NG | 19.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chloral hydrate | µg/L | ≤ 100 | NG | 8.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chloride | mg/L | NG | ≤ 250 | 51 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Colour | HU | NG | ≤ 15 | 2 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Copper | mg/L | ≤ 2 | ≤ 1 | 0.4046 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Dichloroacetic acid | µg/L | ≤ 100 | NG | 2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Fluoride | mg/L | ≤ 1.5 | NG | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Hardness | mg/L | NG | ≤ 200 | 89 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Iodide | mg/L | ≤ 0.5 | NG | 0.02 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Iron | mg/L | NG | ≤ 0.3 | 0.4844 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Magnesium | mg/L | NG | NG | 9.87 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0157 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Nickel | mg/L | ≤ 0.02 | NG | 0.0014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.22 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Potassium | mg/L | NG | NG | 8.34 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Silica - reactive | mg/L | NG | ≤ 80 | 3.06 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Sodium | mg/L | NG | ≤ 180 | 60.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Sulphate | mg/L | NG | ≤ 250 | 71.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Total dissolved solids | mg/L | NG | ≤ 600 | 278 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Trichloroacetic acid | µg/L | ≤ 100 | NG | 16 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 120 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Turbidity | NTU | NG | ≤ 5 | 1.47 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Zinc | mg/L | NG | ≤ 3 | 0.0832 | NA | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Hardness - English Degrees | °e | NG | NG | 6.23 | NG | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Hardness - French Degrees | °f | NG | NG | 8.9 | NG | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Hardness - German Degrees | °dH | NG | NG | 4.98 | NG | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Gerard | Hardness - International | PPM or mg/L | NG | NG | 89 | NG | Chlorine | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Alkalinity | mg/L | NG | NG | 67 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.015 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Barium | mg/L | ≤ 2 | NG | 0.0009 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Bicarbonate | mg/L | NG | NG | 81 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Boron | mg/L | ≤ 4 | NG | 0.387 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Calcium | mg/L | NG | NG | 22.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Chloride | mg/L | NG | ≤ 250 | 10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0212 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Hardness | mg/L | NG | ≤ 200 | 58 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Iron | mg/L | NG | ≤ 0.3 | 0.0487 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Lead | mg/L | ≤ 0.01 | NG | 0.0011 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Magnesium | mg/L | NG | NG | 0.35 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0014 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 2.58 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Potassium | mg/L | NG | NG | 0.82 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Silica - reactive | mg/L | NG | ≤ 80 | 1.26 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Sodium | mg/L | NG | ≤ 180 | 9.66 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Sulphate | mg/L | NG | ≤ 250 | <0.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Total dissolved solids | mg/L | NG | ≤ 600 | 89 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Turbidity | NTU | NG | ≤ 5 | 0.97 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Zinc | mg/L | NG | ≤ 3 | 0.0579 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Hardness - English Degrees | °e | NG | NG | 4.06 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Hardness - French Degrees | °f | NG | NG | 5.8 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Hardness - German Degrees | °dH | NG | NG | 3.25 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Indulkana | Hardness - International | PPM or mg/L | NG | NG | 58 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Alkalinity | mg/L | NG | NG | 307 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.018 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Arsenic | mg/L | ≤ 0.01 | NG | 0.00132 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Barium | mg/L | ≤ 2 | NG | 0.0783 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Bicarbonate | mg/L | NG | NG | 374 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Boron | mg/L | ≤ 4 | NG | 0.132 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Calcium | mg/L | NG | NG | 48.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Chloride | mg/L | NG | ≤ 250 | 126 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Chromium | mg/L | ≤ 0.05 | NG | 0.0051 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0031 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Fluoride | mg/L | ≤ 1.5 | NG | 1.0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Hardness | mg/L | NG | ≤ 200 | 369 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Iron | mg/L | NG | ≤ 0.3 | 0.0298 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Lead | mg/L | ≤ 0.01 | NG | 0.0012 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Magnesium | mg/L | NG | NG | 60.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0197 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0019 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 28.56 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Potassium | mg/L | NG | NG | 2.98 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Selenium | mg/L | ≤ 0.01 | NG | 0.0032 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Silica - reactive | mg/L | NG | ≤ 80 | 66.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Sodium | mg/L | NG | ≤ 180 | 86.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Sulphate | mg/L | NG | ≤ 250 | 54.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Total dissolved solids | mg/L | NG | ≤ 600 | 599 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Turbidity | NTU | NG | ≤ 5 | 0.34 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Uranium | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Zinc | mg/L | NG | ≤ 3 | 0.0060 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Hardness - English Degrees | °e | NG | NG | 25.83 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Hardness - French Degrees | °f | NG | NG | 36.9 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Hardness - German Degrees | °dH | NG | NG | 20.66 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kalka | Hardness - International | PPM or mg/L | NG | NG | 369 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Alkalinity | mg/L | NG | NG | 88 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Barium | mg/L | ≤ 2 | NG | 0.0225 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Bicarbonate | mg/L | NG | NG | 108 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Boron | mg/L | ≤ 4 | NG | 0.257 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Calcium | mg/L | NG | NG | 19.2 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Chloride | mg/L | NG | ≤ 250 | 145 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Chromium | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0079 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Hardness | mg/L | NG | ≤ 200 | 118 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Iron | mg/L | NG | ≤ 0.3 | <0.0005 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Magnesium | mg/L | NG | NG | 17.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Nickel | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 17.38 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Potassium | mg/L | NG | NG | 6.39 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Selenium | mg/L | ≤ 0.01 | NG | 0.0015 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Silica - reactive | mg/L | NG | ≤ 80 | 28.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Sodium | mg/L | NG | ≤ 180 | 105 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Sulphate | mg/L | NG | ≤ 250 | 39.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Total dissolved solids | mg/L | NG | ≤ 600 | 432 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Uranium | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Zinc | mg/L | NG | ≤ 3 | 0.0056 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Hardness - English Degrees | °e | NG | NG | 8.26 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Hardness - French Degrees | °f | NG | NG | 11.8 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Hardness - German Degrees | °dH | NG | NG | 6.61 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Kaltjiti | Hardness - International | PPM or mg/L | NG | NG | 118 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Alkalinity | mg/L | NG | NG | 51 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Arsenic | mg/L | ≤ 0.01 | NG | 0.00029 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Barium | mg/L | ≤ 2 | NG | 0.0088 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Bicarbonate | mg/L | NG | NG | 62 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Boron | mg/L | ≤ 4 | NG | 0.376 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Calcium | mg/L | NG | NG | 7.99 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Chloride | mg/L | NG | ≤ 250 | 77 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Chromium | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0336 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Hardness | mg/L | NG | ≤ 200 | 48 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Iron | mg/L | NG | ≤ 0.3 | <0.0005 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Magnesium | mg/L | NG | NG | 6.88 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 24.07 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Potassium | mg/L | NG | NG | 4.69 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Selenium | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Silica - reactive | mg/L | NG | ≤ 80 | 18.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Sodium | mg/L | NG | ≤ 180 | 68.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Sulphate | mg/L | NG | ≤ 250 | 22.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Total dissolved solids | mg/L | NG | ≤ 600 | 257 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Uranium | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Zinc | mg/L | NG | ≤ 3 | 0.0085 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Hardness - English Degrees | °e | NG | NG | 3.36 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Hardness - French Degrees | °f | NG | NG | 4.8 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Hardness - German Degrees | °dH | NG | NG | 2.69 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Mimili | Hardness - International | PPM or mg/L | NG | NG | 48 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Alkalinity | mg/L | NG | NG | 108 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.003 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Barium | mg/L | ≤ 2 | NG | 0.0223 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Bicarbonate | mg/L | NG | NG | 132 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Boron | mg/L | ≤ 4 | NG | 0.173 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Calcium | mg/L | NG | NG | 15.4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Chloride | mg/L | NG | ≤ 250 | 68 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Chromium | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0552 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Hardness | mg/L | NG | ≤ 200 | 92 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Iron | mg/L | NG | ≤ 0.3 | 0.0011 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Lead | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Magnesium | mg/L | NG | NG | 13.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Nickel | mg/L | ≤ 0.02 | NG | 0.0010 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 5.08 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | pH | pH units | NG | 6.5 - 8.5 | 8.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Potassium | mg/L | NG | NG | 3.39 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Selenium | mg/L | ≤ 0.01 | NG | 0.0012 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Silica - reactive | mg/L | NG | ≤ 80 | 16.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Sodium | mg/L | NG | ≤ 180 | 58.2 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Sulphate | mg/L | NG | ≤ 250 | 20.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Total dissolved solids | mg/L | NG | ≤ 600 | 265 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Uranium | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Zinc | mg/L | NG | ≤ 3 | 0.0149 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Hardness - English Degrees | °e | NG | NG | 6.44 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Hardness - French Degrees | °f | NG | NG | 9.2 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Hardness - German Degrees | °dH | NG | NG | 5.15 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Murputja | Hardness - International | PPM or mg/L | NG | NG | 92 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Alkalinity | mg/L | NG | NG | 10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.137 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Barium | mg/L | ≤ 2 | NG | 0.0129 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Bicarbonate | mg/L | NG | NG | 12 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Cadmium | mg/L | ≤ 0.002 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Calcium | mg/L | NG | NG | 1.76 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Chloride | mg/L | NG | ≤ 250 | 4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Chromium | mg/L | ≤ 0.05 | NG | 0.0015 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Copper | mg/L | ≤ 2 | ≤ 1 | 0.1225 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Hardness | mg/L | NG | ≤ 200 | 6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Iron | mg/L | NG | ≤ 0.3 | 0.2628 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Lanthanum | mg/L | ≤ 0.002 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Lead | mg/L | ≤ 0.01 | NG | 0.0034 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Magnesium | mg/L | NG | NG | 0.39 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0068 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.80 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | pH | pH units | NG | 6.5 - 8.5 | 7.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Potassium | mg/L | NG | NG | 0.17 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Selenium | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Silica - reactive | mg/L | NG | ≤ 80 | 0.54 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Sodium | mg/L | NG | ≤ 180 | 3.93 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Sulphate | mg/L | NG | ≤ 250 | 0.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Total dissolved solids | mg/L | NG | ≤ 600 | 20 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Turbidity | NTU | NG | ≤ 5 | 1.91 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Zinc | mg/L | NG | ≤ 3 | 2.5070 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Hardness - English Degrees | °e | NG | NG | 0.42 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Hardness - French Degrees | °f | NG | NG | 0.6 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Hardness - German Degrees | °dH | NG | NG | 0.34 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Nepabunna | Hardness - International | PPM or mg/L | NG | NG | 6 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Alkalinity | mg/L | NG | NG | 8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Antimony | mg/L | ≤ 0.003 | NG | 0.0009 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Barium | mg/L | ≤ 2 | NG | 0.0019 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Bicarbonate | mg/L | NG | NG | 10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Boron | mg/L | ≤ 4 | NG | <0.020 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Calcium | mg/L | NG | NG | 1.42 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Chloride | mg/L | NG | ≤ 250 | <4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Copper | mg/L | ≤ 2 | ≤ 1 | 0.3967 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Hardness | mg/L | NG | ≤ 200 | 4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Iron | mg/L | NG | ≤ 0.3 | < 0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Lead | mg/L | ≤ 0.01 | NG | 0.0017 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Magnesium | mg/L | NG | NG | 0.19 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0014 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 2.04 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | pH | pH units | NG | 6.5 - 8.5 | 6.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Potassium | mg/L | NG | NG | 0.09 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Silica - reactive | mg/L | NG | ≤ 80 | 0.52 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Sodium | mg/L | NG | ≤ 180 | 0.97 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Sulphate | mg/L | NG | ≤ 250 | <0.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Total dissolved solids | mg/L | NG | ≤ 600 | 14 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Turbidity | NTU | NG | ≤ 5 | 0.14 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Zinc | mg/L | NG | ≤ 3 | 1.9590 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Hardness - English Degrees | °e | NG | NG | 0.28 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Hardness - French Degrees | °f | NG | NG | 0.4 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Hardness - German Degrees | °dH | NG | NG | 0.22 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Oak Valley | Hardness - International | PPM or mg/L | NG | NG | 4 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Alkalinity | mg/L | NG | NG | 367 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Barium | mg/L | ≤ 2 | NG | 0.0528 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Bicarbonate | mg/L | NG | NG | 448 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Boron | mg/L | ≤ 4 | NG | 0.134 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Calcium | mg/L | NG | NG | 36.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Chloride | mg/L | NG | ≤ 250 | 148 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Chromium | mg/L | ≤ 0.05 | NG | 0.0053 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0109 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Hardness | mg/L | NG | ≤ 200 | 407 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Iron | mg/L | NG | ≤ 0.3 | < 0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Lead | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Magnesium | mg/L | NG | NG | 76.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0012 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 30.68 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | pH | pH units | NG | 6.5 - 8.5 | 7.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Potassium | mg/L | NG | NG | 3.11 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Selenium | mg/L | ≤ 0.01 | NG | 0.0040 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Silica - reactive | mg/L | NG | ≤ 80 | 72.7 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Sodium | mg/L | NG | ≤ 180 | 109 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Sulphate | mg/L | NG | ≤ 250 | 58.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Total dissolved solids | mg/L | NG | ≤ 600 | 714 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Uranium | mg/L | ≤ 0.02 | NG | 0.0011 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Zinc | mg/L | NG | ≤ 3 | 0.0091 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Hardness - English Degrees | °e | NG | NG | 28.49 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Hardness - French Degrees | °f | NG | NG | 40.7 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Hardness - German Degrees | °dH | NG | NG | 22.79 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pipalyatjara | Hardness - International | PPM or mg/L | NG | NG | 407 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pt Pearce | Alkalinity | mg/L | NG | NG | 61 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Bicarbonate | mg/L | NG | NG | 61 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Calcium | mg/L | NG | NG | 16.4 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Carbonate | mg/L | NG | NG | 7 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.4 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.4 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.88 | 100% | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | pH | pH units | NG | 6.5 - 8.5 | 9.0 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Total dissolved solids | mg/L | NG | ≤ 600 | 201 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Hardness - English Degrees | °e | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Hardness - French Degrees | °f | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Hardness - German Degrees | °dH | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pt Pearce | Hardness - International | PPM or mg/L | NG | NG | NA | NG | Chloramine | 01/04/2022 - 31/03/2023 | Fed from Morgan/Swan Reach system, for more data search Morgan/Swan Reach
Remote Communities | Pukatja | Alkalinity | mg/L | NG | NG | 383 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Arsenic | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Barium | mg/L | ≤ 2 | NG | 0.0183 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Bicarbonate | mg/L | NG | NG | 468 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Boron | mg/L | ≤ 4 | NG | 0.160 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Calcium | mg/L | NG | NG | 46.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Chloride | mg/L | NG | ≤ 250 | 92 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0084 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Fluoride | mg/L | ≤ 1.5 | NG | 1.2 | 75.0% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Hardness | mg/L | NG | ≤ 200 | 270 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Iron | mg/L | NG | ≤ 0.3 | 0.0015 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Magnesium | mg/L | NG | NG | 37.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0031 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 5.47 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Potassium | mg/L | NG | NG | 1.79 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Selenium | mg/L | ≤ 0.01 | NG | 0.0015 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Silica - reactive | mg/L | NG | ≤ 80 | 71.7 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Sodium | mg/L | NG | ≤ 180 | 149 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Sulphate | mg/L | NG | ≤ 250 | 72.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Total dissolved solids | mg/L | NG | ≤ 600 | 616 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Uranium | mg/L | ≤ 0.02 | NG | 0.0012 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Zinc | mg/L | NG | ≤ 3 | 0.0725 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Hardness - English Degrees | °e | NG | NG | 18.90 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Hardness - French Degrees | °f | NG | NG | 27.0 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Hardness - German Degrees | °dH | NG | NG | 15.12 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Pukatja | Hardness - International | PPM or mg/L | NG | NG | 270 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Raukkan | Alkalinity | mg/L | NG | NG | 50 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Bicarbonate | mg/L | NG | NG | 55 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Calcium | mg/L | NG | NG | 13.3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Carbonate | mg/L | NG | NG | 3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.94 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | pH | pH units | NG | 6.5 - 8.5 | 8.9 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Total dissolved solids | mg/L | NG | ≤ 600 | 175 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Turbidity | NTU | NG | ≤ 5 | 0.11 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Hardness - English Degrees | °e | NG | NG | NA | NG | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Hardness - French Degrees | °f | NG | NG | NA | NG | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Hardness - German Degrees | °dH | NG | NG | NA | NG | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Raukkan | Hardness - International | PPM or mg/L | NG | NG | NA | NG | Chloramine / UV | 01/04/2022 - 31/03/2023 | Fed from Tailem Bend system, for more data search Tailem Bend.
Remote Communities | Umuwa | Alkalinity | mg/L | NG | NG | 272 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Barium | mg/L | ≤ 2 | NG | 0.0143 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Bicarbonate | mg/L | NG | NG | 328 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Boron | mg/L | ≤ 4 | NG | 0.135 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Calcium | mg/L | NG | NG | 44.2 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Carbonate | mg/L | NG | NG | 2 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Chloride | mg/L | NG | ≤ 250 | 30 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0100 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Fluoride | mg/L | ≤ 1.5 | NG | 0.9 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Hardness | mg/L | NG | ≤ 200 | 241 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Iron | mg/L | NG | ≤ 0.3 | 0.0057 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Lead | mg/L | ≤ 0.01 | NG | 0.0004 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Magnesium | mg/L | NG | NG | 31.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0007 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 14.75 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | pH | pH units | NG | 6.5 - 8.5 | 8.3 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Potassium | mg/L | NG | NG | 4.09 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Selenium | mg/L | ≤ 0.01 | NG | 0.0014 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Silica - reactive | mg/L | NG | ≤ 80 | 57.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Sodium | mg/L | NG | ≤ 180 | 45.6 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Sulphate | mg/L | NG | ≤ 250 | 20.1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Total dissolved solids | mg/L | NG | ≤ 600 | 359 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Uranium | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Zinc | mg/L | NG | ≤ 3 | 0.0204 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Hardness - English Degrees | °e | NG | NG | 16.87 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Hardness - French Degrees | °f | NG | NG | 24.1 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Hardness - German Degrees | °dH | NG | NG | 13.50 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Umuwa | Hardness - International | PPM or mg/L | NG | NG | 241 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Alkalinity | mg/L | NG | NG | 336 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.007 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Arsenic | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Barium | mg/L | ≤ 2 | NG | 0.1382 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Bicarbonate | mg/L | NG | NG | 410 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Boron | mg/L | ≤ 4 | NG | 0.146 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Calcium | mg/L | NG | NG | 45.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Chloride | mg/L | NG | ≤ 250 | 219 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Chromium | mg/L | ≤ 0.05 | NG | 0.0027 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0312 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Fluoride | mg/L | ≤ 1.5 | NG | 1.3 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Hardness | mg/L | NG | ≤ 200 | 459 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Iron | mg/L | NG | ≤ 0.3 | 0.0007 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Magnesium | mg/L | NG | NG | 83.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 15.62 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | pH | pH units | NG | 6.5 - 8.5 | 7.9 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Potassium | mg/L | NG | NG | 6.45 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Selenium | mg/L | ≤ 0.01 | NG | 0.0030 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Silica - reactive | mg/L | NG | ≤ 80 | 82.0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Sodium | mg/L | NG | ≤ 180 | 130 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Sulphate | mg/L | NG | ≤ 250 | 106.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Total dissolved solids | mg/L | NG | ≤ 600 | 849 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Uranium | mg/L | ≤ 0.02 | NG | 0.0024 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Zinc | mg/L | NG | ≤ 3 | 0.0050 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Hardness - English Degrees | °e | NG | NG | 32.13 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Hardness - French Degrees | °f | NG | NG | 45.9 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Hardness - German Degrees | °dH | NG | NG | 25.70 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Watinuma | Hardness - International | PPM or mg/L | NG | NG | 459 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Alkalinity | mg/L | NG | NG | 113 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Barium | mg/L | ≤ 2 | NG | <0.0005 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Bicarbonate | mg/L | NG | NG | 138 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Boron | mg/L | ≤ 4 | NG | 0.150 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Calcium | mg/L | NG | NG | 41.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Chloride | mg/L | NG | ≤ 250 | 22 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0107 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Fluoride | mg/L | ≤ 1.5 | NG | <0.10 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Hardness | mg/L | NG | ≤ 200 | 109 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Iron | mg/L | NG | ≤ 0.3 | 0.0013 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Magnesium | mg/L | NG | NG | 1.29 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Nickel | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.06 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | pH | pH units | NG | 6.5 - 8.5 | 7.7 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Potassium | mg/L | NG | NG | 0.44 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Silica - reactive | mg/L | NG | ≤ 80 | 0.21 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Silver | mg/L | ≤ 0.1 | NG | <0.00003 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Sodium | mg/L | NG | ≤ 180 | 13.3 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Sulphate | mg/L | NG | ≤ 250 | 1.5 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Total dissolved solids | mg/L | NG | ≤ 600 | 153 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Zinc | mg/L | NG | ≤ 3 | 0.0046 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Hardness - English Degrees | °e | NG | NG | 7.63 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Hardness - French Degrees | °f | NG | NG | 10.9 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Hardness - German Degrees | °dH | NG | NG | 6.10 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yalata | Hardness - International | PPM or mg/L | NG | NG | 109 | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Alkalinity | mg/L | NG | NG | 32 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Bicarbonate | mg/L | NG | NG | 39 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Carbonate | mg/L | NG | NG | 0 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Chloride | mg/L | NG | ≤ 250 | <4 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Colour | HU | NG | ≤ 15 | <1 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | E. coli | MPN/100mL | 0 | NG | 0 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Fluoride | mg/L | ≤ 1.5 | NG | 0.39 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 10.06 | 100% | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Silica - reactive | mg/L | NG | ≤ 80 | 2.48 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Total dissolved solids | mg/L | NG | ≤ 600 | 33 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Turbidity | NTU | NG | ≤ 5 | 0.27 | NA | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Hardness - English Degrees | °e | NG | NG | NA | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Hardness - French Degrees | °f | NG | NG | NA | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Hardness - German Degrees | °dH | NG | NG | NA | NG | UV | 01/04/2022 - 31/03/2023
Remote Communities | Yunyarinyi | Hardness - International | PPM or mg/L | NG | NG | NA | NG | UV | 01/04/2022 - 31/03/2023
South East | Beachport | Alkalinity | mg/L | NG | NG | 325 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Barium | mg/L | ≤ 2 | NG | 0.0582 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Bicarbonate | mg/L | NG | NG | 397 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Boron | mg/L | ≤ 4 | NG | 0.191 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Calcium | mg/L | NG | NG | 80.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chloride | mg/L | NG | ≤ 250 | 173 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0231 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Fluoride | mg/L | ≤ 1.5 | NG | 0.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Hardness | mg/L | NG | ≤ 200 | 276 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Iron | mg/L | NG | ≤ 0.3 | 0.0062 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Lead | mg/L | ≤ 0.01 | NG | 0.0015 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Magnesium | mg/L | NG | NG | 18.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Nickel | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.08 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Potassium | mg/L | NG | NG | 10.17 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Silica - reactive | mg/L | NG | ≤ 80 | 16.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Sodium | mg/L | NG | ≤ 180 | 136 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Sulphate | mg/L | NG | ≤ 250 | 22.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Total dissolved solids | mg/L | NG | ≤ 600 | 672 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 42 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Zinc | mg/L | NG | ≤ 3 | 0.0065 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Hardness - English Degrees | °e | NG | NG | 19.32 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Hardness - French Degrees | °f | NG | NG | 27.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Hardness - German Degrees | °dH | NG | NG | 15.46 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Beachport | Hardness - International | PPM or mg/L | NG | NG | 276 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Alkalinity | mg/L | NG | NG | 279 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.003 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Antimony | mg/L | ≤ 0.003 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Barium | mg/L | ≤ 2 | NG | 0.0301 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Bicarbonate | mg/L | NG | NG | 340 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Boron | mg/L | ≤ 4 | NG | 0.108 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Calcium | mg/L | NG | NG | 73.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chloride | mg/L | NG | ≤ 250 | 102 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0057 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Fluoride | mg/L | ≤ 1.5 | NG | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Hardness | mg/L | NG | ≤ 200 | 260 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Iron | mg/L | NG | ≤ 0.3 | 0.0022 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Magnesium | mg/L | NG | NG | 18.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Nickel | mg/L | ≤ 0.02 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.14 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | pH | pH units | NG | 6.5 - 8.5 | 7.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Potassium | mg/L | NG | NG | 4.61 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Selenium | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Silica - reactive | mg/L | NG | ≤ 80 | 19.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Sodium | mg/L | NG | ≤ 180 | 73.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Sulphate | mg/L | NG | ≤ 250 | 15.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Total dissolved solids | mg/L | NG | ≤ 600 | 487 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 17 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Uranium | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Zinc | mg/L | NG | ≤ 3 | 0.0021 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Hardness - English Degrees | °e | NG | NG | 18.20 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Hardness - French Degrees | °f | NG | NG | 26.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Hardness - German Degrees | °dH | NG | NG | 14.56 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Bordertown | Hardness - International | PPM or mg/L | NG | NG | 260 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Alkalinity | mg/L | NG | NG | 520 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Arsenic | mg/L | ≤ 0.01 | NG | 0.00076 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Barium | mg/L | ≤ 2 | NG | 0.0046 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Bicarbonate | mg/L | NG | NG | 634 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Boron | mg/L | ≤ 4 | NG | 0.239 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Calcium | mg/L | NG | NG | 104 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chloride | mg/L | NG | ≤ 250 | 482 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Chromium | mg/L | ≤ 0.05 | NG | 0.0032 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0430 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Fluoride | mg/L | ≤ 1.5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Hardness | mg/L | NG | ≤ 200 | 586 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Iron | mg/L | NG | ≤ 0.3 | 0.0076 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Lead | mg/L | ≤ 0.01 | NG | 0.0010 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Magnesium | mg/L | NG | NG | 79.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Nickel | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.22 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | pH | pH units | NG | 6.5 - 8.5 | 7.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Potassium | mg/L | NG | NG | 10.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Selenium | mg/L | ≤ 0.01 | NG | 0.0031 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Silica - reactive | mg/L | NG | ≤ 80 | 29.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Sodium | mg/L | NG | ≤ 180 | 325 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Sulphate | mg/L | NG | ≤ 250 | 123.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Total dissolved solids | mg/L | NG | ≤ 600 | 1,443 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | <4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Uranium | mg/L | ≤ 0.02 | NG | 0.0016 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Zinc | mg/L | NG | ≤ 3 | 0.0286 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Hardness - English Degrees | °e | NG | NG | 41.02 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Hardness - French Degrees | °f | NG | NG | 58.6 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Hardness - German Degrees | °dH | NG | NG | 32.82 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Geranium | Hardness - International | PPM or mg/L | NG | NG | 586 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Alkalinity | mg/L | NG | NG | 349 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.008 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Barium | mg/L | ≤ 2 | NG | 0.0164 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Bicarbonate | mg/L | NG | NG | 425 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Boron | mg/L | ≤ 4 | NG | 0.031 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Calcium | mg/L | NG | NG | 122 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chloride | mg/L | NG | ≤ 250 | 110 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0152 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Dichloroacetic acid | µg/L | ≤ 100 | NG | 2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Fluoride | mg/L | ≤ 1.5 | NG | 0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Hardness | mg/L | NG | ≤ 200 | 350 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Iodide | mg/L | ≤ 0.5 | NG | 0.04 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Iron | mg/L | NG | ≤ 0.3 | 0.0092 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Lead | mg/L | ≤ 0.01 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Magnesium | mg/L | NG | NG | 11.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Nickel | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.03 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | pH | pH units | NG | 6.5 - 8.5 | 7.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Potassium | mg/L | NG | NG | 1.64 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Silica - reactive | mg/L | NG | ≤ 80 | 12.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Sodium | mg/L | NG | ≤ 180 | 63.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Sulphate | mg/L | NG | ≤ 250 | 7.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Total dissolved solids | mg/L | NG | ≤ 600 | 552 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 67 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Zinc | mg/L | NG | ≤ 3 | 0.0088 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Hardness - English Degrees | °e | NG | NG | 24.50 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Hardness - French Degrees | °f | NG | NG | 35.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Hardness - German Degrees | °dH | NG | NG | 19.60 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kalangadoo | Hardness - International | PPM or mg/L | NG | NG | 350 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Alkalinity | mg/L | NG | NG | 301 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Barium | mg/L | ≤ 2 | NG | 0.0545 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Beryllium | mg/L | ≤ 0.06 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Bicarbonate | mg/L | NG | NG | 367 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Boron | mg/L | ≤ 4 | NG | 0.253 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Calcium | mg/L | NG | NG | 64.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Chloride | mg/L | NG | ≤ 250 | 274 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0239 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Fluoride | mg/L | ≤ 1.5 | NG | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Hardness | mg/L | NG | ≤ 200 | 234 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Iodide | mg/L | ≤ 0.5 | NG | 0.04 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Iron | mg/L | NG | ≤ 0.3 | 0.0032 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Magnesium | mg/L | NG | NG | 17.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Nickel | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.08 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | pH | pH units | NG | 6.5 - 8.5 | 7.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Potassium | mg/L | NG | NG | 13.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Silica - reactive | mg/L | NG | ≤ 80 | 13.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Sodium | mg/L | NG | ≤ 180 | 207 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Sulphate | mg/L | NG | ≤ 250 | 30.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Total dissolved solids | mg/L | NG | ≤ 600 | 837 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 40 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Zinc | mg/L | NG | ≤ 3 | 0.0087 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Hardness - English Degrees | °e | NG | NG | 16.38 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Hardness - French Degrees | °f | NG | NG | 23.4 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Hardness - German Degrees | °dH | NG | NG | 13.10 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Kingston SE | Hardness - International | PPM or mg/L | NG | NG | 234 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Alkalinity | mg/L | NG | NG | 232 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Arsenic | mg/L | ≤ 0.01 | NG | 0.00691 | 91.7% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Barium | mg/L | ≤ 2 | NG | 0.0054 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Bicarbonate | mg/L | NG | NG | 283 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Boron | mg/L | ≤ 4 | NG | 0.167 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Calcium | mg/L | NG | NG | 47.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chloride | mg/L | NG | ≤ 250 | 356 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0105 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Fluoride | mg/L | ≤ 1.5 | NG | 0.6 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Hardness | mg/L | NG | ≤ 200 | 244 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Iron | mg/L | NG | ≤ 0.3 | 0.1361 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Magnesium | mg/L | NG | NG | 30.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Mercury | mg/L | ≤ 0.001 | NG | 0.00004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | <0.014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | pH | pH units | NG | 6.5 - 8.5 | 7.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Potassium | mg/L | NG | NG | 7.65 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Silica - reactive | mg/L | NG | ≤ 80 | 23.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Sodium | mg/L | NG | ≤ 180 | 264 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Sulphate | mg/L | NG | ≤ 250 | 85.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Total dissolved solids | mg/L | NG | ≤ 600 | 971 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 24 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Turbidity | NTU | NG | ≤ 5 | 0.35 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Zinc | mg/L | NG | ≤ 3 | 0.0062 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Hardness - English Degrees | °e | NG | NG | 17.08 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Hardness - French Degrees | °f | NG | NG | 24.4 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Hardness - German Degrees | °dH | NG | NG | 13.66 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lameroo | Hardness - International | PPM or mg/L | NG | NG | 244 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Alkalinity | mg/L | NG | NG | 318 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Barium | mg/L | ≤ 2 | NG | 0.0298 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Bicarbonate | mg/L | NG | NG | 388 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Boron | mg/L | ≤ 4 | NG | 0.195 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Calcium | mg/L | NG | NG | 80.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Chloride | mg/L | NG | ≤ 250 | 283 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0202 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Fluoride | mg/L | ≤ 1.5 | NG | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Hardness | mg/L | NG | ≤ 200 | 328 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Iron | mg/L | NG | ≤ 0.3 | 0.0045 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Lead | mg/L | ≤ 0.01 | NG | 0.0012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Magnesium | mg/L | NG | NG | 30.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Nickel | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Potassium | mg/L | NG | NG | 7.81 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Silica - reactive | mg/L | NG | ≤ 80 | 11.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Sodium | mg/L | NG | ≤ 180 | 178 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Sulphate | mg/L | NG | ≤ 250 | 7.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Total dissolved solids | mg/L | NG | ≤ 600 | 830 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 105 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Zinc | mg/L | NG | ≤ 3 | 0.0279 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Hardness - English Degrees | °e | NG | NG | 22.96 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Hardness - French Degrees | °f | NG | NG | 32.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Hardness - German Degrees | °dH | NG | NG | 18.37 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Lucindale | Hardness - International | PPM or mg/L | NG | NG | 328 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Alkalinity | mg/L | NG | NG | 298 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.003 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Arsenic | mg/L | ≤ 0.01 | NG | 0.00201 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Barium | mg/L | ≤ 2 | NG | 0.0058 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Bicarbonate | mg/L | NG | NG | 364 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Calcium | mg/L | NG | NG | 81.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chloride | mg/L | NG | ≤ 250 | 143 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0200 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Fluoride | mg/L | ≤ 1.5 | NG | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Hardness | mg/L | NG | ≤ 200 | 382 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Iodide | mg/L | ≤ 0.5 | NG | 0.02 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Iron | mg/L | NG | ≤ 0.3 | 0.0319 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Magnesium | mg/L | NG | NG | 43.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0016 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Nickel | mg/L | ≤ 0.02 | NG | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.47 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Potassium | mg/L | NG | NG | 4.94 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Selenium | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Silica - reactive | mg/L | NG | ≤ 80 | 30.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Sodium | mg/L | NG | ≤ 180 | 83.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Sulphate | mg/L | NG | ≤ 250 | 86.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Total dissolved solids | mg/L | NG | ≤ 600 | 644 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 81 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Uranium | mg/L | ≤ 0.02 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Zinc | mg/L | NG | ≤ 3 | 0.0072 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Hardness - English Degrees | °e | NG | NG | 26.74 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Hardness - French Degrees | °f | NG | NG | 38.2 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Hardness - German Degrees | °dH | NG | NG | 21.39 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Millicent | Hardness - International | PPM or mg/L | NG | NG | 382 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Alkalinity | mg/L | NG | NG | 282 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Arsenic | mg/L | ≤ 0.01 | NG | 0.00063 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Barium | mg/L | ≤ 2 | NG | 0.0139 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Bicarbonate | mg/L | NG | NG | 344 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Boron | mg/L | ≤ 4 | NG | 0.025 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Calcium | mg/L | NG | NG | 83.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chloride | mg/L | NG | ≤ 250 | 84 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chlorine (total residual) | mg/L | ≤ 5 | NG | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Chromium | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0019 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Fluoride | mg/L | ≤ 1.5 | NG | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Hardness | mg/L | NG | ≤ 200 | 278 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Iron | mg/L | NG | ≤ 0.3 | 0.0028 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Magnesium | mg/L | NG | NG | 16.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 3.88 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Potassium | mg/L | NG | NG | 1.92 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Selenium | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Silica - reactive | mg/L | NG | ≤ 80 | 22.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Sodium | mg/L | NG | ≤ 180 | 55.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Sulphate | mg/L | NG | ≤ 250 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Total dissolved solids | mg/L | NG | ≤ 600 | 458 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 5 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Uranium | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Zinc | mg/L | NG | ≤ 3 | 0.0059 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Hardness - English Degrees | °e | NG | NG | 19.46 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Hardness - French Degrees | °f | NG | NG | 27.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Hardness - German Degrees | °dH | NG | NG | 15.57 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Burr | Hardness - International | PPM or mg/L | NG | NG | 278 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Alkalinity | mg/L | NG | NG | 176 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Arsenic | mg/L | ≤ 0.01 | NG | 0.00064 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Barium | mg/L | ≤ 2 | NG | 0.0048 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Bicarbonate | mg/L | NG | NG | 214 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Boron | mg/L | ≤ 4 | NG | 0.025 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Calcium | mg/L | NG | NG | 43.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Carbonate | mg/L | NG | NG | 1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Chloride | mg/L | NG | ≤ 250 | 83 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0047 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Hardness | mg/L | NG | ≤ 200 | 190 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Iron | mg/L | NG | ≤ 0.3 | 0.0044 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Magnesium | mg/L | NG | NG | 19.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0008 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Nickel | mg/L | ≤ 0.02 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 12.76 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | pH | pH units | NG | 6.5 - 8.5 | 8.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Potassium | mg/L | NG | NG | 3.02 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Selenium | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Silica - reactive | mg/L | NG | ≤ 80 | 16.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Sodium | mg/L | NG | ≤ 180 | 57.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Sulphate | mg/L | NG | ≤ 250 | 15.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Total dissolved solids | mg/L | NG | ≤ 600 | 369 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 20 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Turbidity | NTU | NG | ≤ 5 | 0.11 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Uranium | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Zinc | mg/L | NG | ≤ 3 | 0.0034 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Hardness - English Degrees | °e | NG | NG | 13.30 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Hardness - French Degrees | °f | NG | NG | 19.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Hardness - German Degrees | °dH | NG | NG | 10.64 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Mt Gambier | Hardness - International | PPM or mg/L | NG | NG | 190 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Alkalinity | mg/L | NG | NG | 368 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Barium | mg/L | ≤ 2 | NG | 0.0111 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Bicarbonate | mg/L | NG | NG | 449 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Boron | mg/L | ≤ 4 | NG | 0.026 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Calcium | mg/L | NG | NG | 126 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chloride | mg/L | NG | ≤ 250 | 113 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0099 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Fluoride | mg/L | ≤ 1.5 | NG | 0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Hardness | mg/L | NG | ≤ 200 | 367 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Iron | mg/L | NG | ≤ 0.3 | 0.0009 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Lead | mg/L | ≤ 0.01 | NG | 0.0011 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Magnesium | mg/L | NG | NG | 12.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Nickel | mg/L | ≤ 0.02 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 8.44 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Potassium | mg/L | NG | NG | 2.16 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Selenium | mg/L | ≤ 0.01 | NG | 0.0016 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Silica - reactive | mg/L | NG | ≤ 80 | 15.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Sodium | mg/L | NG | ≤ 180 | 84.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Sulphate | mg/L | NG | ≤ 250 | 32.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Total dissolved solids | mg/L | NG | ≤ 600 | 612 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 25 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Uranium | mg/L | ≤ 0.02 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Zinc | mg/L | NG | ≤ 3 | 0.0070 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Hardness - English Degrees | °e | NG | NG | 25.69 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Hardness - French Degrees | °f | NG | NG | 36.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Hardness - German Degrees | °dH | NG | NG | 20.55 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Nangwarry | Hardness - International | PPM or mg/L | NG | NG | 367 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Alkalinity | mg/L | NG | NG | 304 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Barium | mg/L | ≤ 2 | NG | 0.0350 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Bicarbonate | mg/L | NG | NG | 370 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Boron | mg/L | ≤ 4 | NG | 0.543 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Calcium | mg/L | NG | NG | 55.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Chloride | mg/L | NG | ≤ 250 | 468 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Chromium | mg/L | ≤ 0.05 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Copper | mg/L | ≤ 2 | ≤ 1 | 0.2109 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Fluoride | mg/L | ≤ 1.5 | NG | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Hardness | mg/L | NG | ≤ 200 | 337 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Iron | mg/L | NG | ≤ 0.3 | 0.0824 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Lead | mg/L | ≤ 0.01 | NG | 0.0009 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Magnesium | mg/L | NG | NG | 47.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0173 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.11 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Potassium | mg/L | NG | NG | 18.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Silica - reactive | mg/L | NG | ≤ 80 | 11.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Sodium | mg/L | NG | ≤ 180 | 321 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Sulphate | mg/L | NG | ≤ 250 | 128.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Total dissolved solids | mg/L | NG | ≤ 600 | 1,273 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 200 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Turbidity | NTU | NG | ≤ 5 | 0.52 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Zinc | mg/L | NG | ≤ 3 | 0.0197 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Hardness - English Degrees | °e | NG | NG | 23.59 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Hardness - French Degrees | °f | NG | NG | 33.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Hardness - German Degrees | °dH | NG | NG | 18.87 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Naracoorte | Hardness - International | PPM or mg/L | NG | NG | 337 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Alkalinity | mg/L | NG | NG | 382 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.003 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Arsenic | mg/L | ≤ 0.01 | NG | 0.00119 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Barium | mg/L | ≤ 2 | NG | 0.0582 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Bicarbonate | mg/L | NG | NG | 466 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Boron | mg/L | ≤ 4 | NG | 0.081 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Calcium | mg/L | NG | NG | 155 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chloride | mg/L | NG | ≤ 250 | 682 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0262 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Fluoride | mg/L | ≤ 1.5 | NG | 0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Hardness | mg/L | NG | ≤ 200 | 590 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Iron | mg/L | NG | ≤ 0.3 | 0.0141 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Lead | mg/L | ≤ 0.01 | NG | 0.0017 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Magnesium | mg/L | NG | NG | 49.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Nickel | mg/L | ≤ 0.02 | NG | 0.0004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.52 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Potassium | mg/L | NG | NG | 4.72 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Selenium | mg/L | ≤ 0.01 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Silica - reactive | mg/L | NG | ≤ 80 | 21.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Sodium | mg/L | NG | ≤ 180 | 339 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Sulphate | mg/L | NG | ≤ 250 | 72.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Total dissolved solids | mg/L | NG | ≤ 600 | 1,660 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 12 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Turbidity | NTU | NG | ≤ 5 | 0.24 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Uranium | mg/L | ≤ 0.02 | NG | 0.0007 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Zinc | mg/L | NG | ≤ 3 | 0.0099 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Hardness - English Degrees | °e | NG | NG | 41.30 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Hardness - French Degrees | °f | NG | NG | 59.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Hardness - German Degrees | °dH | NG | NG | 33.04 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Padthaway | Hardness - International | PPM or mg/L | NG | NG | 590 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Alkalinity | mg/L | NG | NG | 176 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Arsenic | mg/L | ≤ 0.01 | NG | 0.00333 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Barium | mg/L | ≤ 2 | NG | 0.0166 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Bicarbonate | mg/L | NG | NG | 214 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Boron | mg/L | ≤ 4 | NG | 0.122 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Calcium | mg/L | NG | NG | 44.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chloride | mg/L | NG | ≤ 250 | 222 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0054 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Fluoride | mg/L | ≤ 1.5 | NG | 0.4 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Hardness | mg/L | NG | ≤ 200 | 188 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Iron | mg/L | NG | ≤ 0.3 | 0.0024 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Lead | mg/L | ≤ 0.01 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Magnesium | mg/L | NG | NG | 19.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0010 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.02 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Potassium | mg/L | NG | NG | 5.52 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Silica - reactive | mg/L | NG | ≤ 80 | 20.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Sodium | mg/L | NG | ≤ 180 | 156 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Sulphate | mg/L | NG | ≤ 250 | 53.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Total dissolved solids | mg/L | NG | ≤ 600 | 653 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 22 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Zinc | mg/L | NG | ≤ 3 | 0.0040 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Hardness - English Degrees | °e | NG | NG | 13.16 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Hardness - French Degrees | °f | NG | NG | 18.8 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Hardness - German Degrees | °dH | NG | NG | 10.53 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Parilla | Hardness - International | PPM or mg/L | NG | NG | 188 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Alkalinity | mg/L | NG | NG | 317 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | <0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Barium | mg/L | ≤ 2 | NG | 0.0211 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Bicarbonate | mg/L | NG | NG | 387 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Boron | mg/L | ≤ 4 | NG | 0.088 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Calcium | mg/L | NG | NG | 95.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Chloride | mg/L | NG | ≤ 250 | 184 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0086 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Fluoride | mg/L | ≤ 1.5 | NG | 0.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Hardness | mg/L | NG | ≤ 200 | 323 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Iron | mg/L | NG | ≤ 0.3 | 0.0450 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Lead | mg/L | ≤ 0.01 | NG | 0.0006 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Magnesium | mg/L | NG | NG | 20.4 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0013 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Mercury | mg/L | ≤ 0.001 | NG | 0.00004 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.04 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | pH | pH units | NG | 6.5 - 8.5 | 7.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Potassium | mg/L | NG | NG | 3.28 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Silica - reactive | mg/L | NG | ≤ 80 | 11.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Sodium | mg/L | NG | ≤ 180 | 116 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Sulphate | mg/L | NG | ≤ 250 | 5.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Total dissolved solids | mg/L | NG | ≤ 600 | 669 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 59 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Zinc | mg/L | NG | ≤ 3 | 0.0042 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Hardness - English Degrees | °e | NG | NG | 22.61 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Hardness - French Degrees | °f | NG | NG | 32.3 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Hardness - German Degrees | °dH | NG | NG | 18.09 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Penola | Hardness - International | PPM or mg/L | NG | NG | 323 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Alkalinity | mg/L | NG | NG | 248 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.001 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Arsenic | mg/L | ≤ 0.01 | NG | 0.00368 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Barium | mg/L | ≤ 2 | NG | 0.0081 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Bicarbonate | mg/L | NG | NG | 303 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Boron | mg/L | ≤ 4 | NG | 0.136 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Calcium | mg/L | NG | NG | 52.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chloride | mg/L | NG | ≤ 250 | 194 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chloramine (mono residual) | mg/L | ≤ 5 | NG | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chlorine (total residual) | mg/L | ≤ 5 | NG | 1.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0054 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Hardness | mg/L | NG | ≤ 200 | 257 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Iodide | mg/L | ≤ 0.5 | NG | 0.02 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Iron | mg/L | NG | ≤ 0.3 | 0.0069 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Magnesium | mg/L | NG | NG | 30.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0015 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Nickel | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | <0.014 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Potassium | mg/L | NG | NG | 6.49 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Silica - reactive | mg/L | NG | ≤ 80 | 28.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Sodium | mg/L | NG | ≤ 180 | 160 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Sulphate | mg/L | NG | ≤ 250 | 85.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Total dissolved solids | mg/L | NG | ≤ 600 | 706 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 17 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Zinc | mg/L | NG | ≤ 3 | 0.0023 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Hardness - English Degrees | °e | NG | NG | 17.99 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Hardness - French Degrees | °f | NG | NG | 25.7 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Hardness - German Degrees | °dH | NG | NG | 14.39 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Pinnaroo | Hardness - International | PPM or mg/L | NG | NG | 257 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Alkalinity | mg/L | NG | NG | 361 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Barium | mg/L | ≤ 2 | NG | 0.0710 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Bicarbonate | mg/L | NG | NG | 436 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Boron | mg/L | ≤ 4 | NG | 0.885 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Calcium | mg/L | NG | NG | 1.91 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Carbonate | mg/L | NG | NG | 2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Chloride | mg/L | NG | ≤ 250 | 167 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0199 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Fluoride | mg/L | ≤ 1.5 | NG | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Hardness | mg/L | NG | ≤ 200 | 21 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Iron | mg/L | NG | ≤ 0.3 | 0.0034 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Lead | mg/L | ≤ 0.01 | NG | 0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Magnesium | mg/L | NG | NG | 3.99 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Molybdenum | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Nickel | mg/L | ≤ 0.02 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.13 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | pH | pH units | NG | 6.5 - 8.5 | 8.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Potassium | mg/L | NG | NG | 13.7 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Silica - reactive | mg/L | NG | ≤ 80 | 13.3 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Sodium | mg/L | NG | ≤ 180 | 265 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Sulphate | mg/L | NG | ≤ 250 | 22.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Total dissolved solids | mg/L | NG | ≤ 600 | 703 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 66 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Turbidity | NTU | NG | ≤ 5 | 0.15 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Zinc | mg/L | NG | ≤ 3 | 0.0063 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Hardness - English Degrees | °e | NG | NG | 1.47 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Hardness - French Degrees | °f | NG | NG | 2.1 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Hardness - German Degrees | °dH | NG | NG | 1.18 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Port MacDonnell | Hardness - International | PPM or mg/L | NG | NG | 21 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Alkalinity | mg/L | NG | NG | 314 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.016 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Arsenic | mg/L | ≤ 0.01 | NG | 0.00012 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Barium | mg/L | ≤ 2 | NG | 0.0343 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Bicarbonate | mg/L | NG | NG | 383 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Boron | mg/L | ≤ 4 | NG | 0.445 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Calcium | mg/L | NG | NG | 23.1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Chloride | mg/L | NG | ≤ 250 | 212 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.8 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Chromium | mg/L | ≤ 0.05 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0172 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Fluoride | mg/L | ≤ 1.5 | NG | 0.3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Hardness | mg/L | NG | ≤ 200 | 130 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Iron | mg/L | NG | ≤ 0.3 | 0.0035 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Magnesium | mg/L | NG | NG | 17.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Nickel | mg/L | ≤ 0.02 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.13 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | pH | pH units | NG | 6.5 - 8.5 | 7.8 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Potassium | mg/L | NG | NG | 19.9 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Silica - reactive | mg/L | NG | ≤ 80 | 17.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Sodium | mg/L | NG | ≤ 180 | 226 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Sulphate | mg/L | NG | ≤ 250 | 22.0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Total dissolved solids | mg/L | NG | ≤ 600 | 736 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 44 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Zinc | mg/L | NG | ≤ 3 | 0.0087 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Hardness - English Degrees | °e | NG | NG | 9.10 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Hardness - French Degrees | °f | NG | NG | 13.0 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Hardness - German Degrees | °dH | NG | NG | 7.28 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Robe | Hardness - International | PPM or mg/L | NG | NG | 130 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Alkalinity | mg/L | NG | NG | 70 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.018 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Ammonia - free - as NH3 | mg/L | NG | ≤ 0.5 | 0.42 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Antimony | mg/L | ≤ 0.003 | NG | <0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Arsenic | mg/L | ≤ 0.01 | NG | 0.00049 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Barium | mg/L | ≤ 2 | NG | 0.0437 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Bicarbonate | mg/L | NG | NG | 71 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Boron | mg/L | ≤ 4 | NG | 0.031 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Calcium | mg/L | NG | NG | 17.7 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Carbonate | mg/L | NG | NG | 7 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Chloride | mg/L | NG | ≤ 250 | 42 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | <0.1 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Chloramine (mono residual) | mg/L | ≤ 5 | NG | 2.8 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Chlorine (total residual) | mg/L | ≤ 5 | NG | 2.9 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Chromium | mg/L | ≤ 0.05 | NG | 0.0002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Colour | HU | NG | ≤ 15 | 2 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0066 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Fluoride | mg/L | ≤ 1.5 | NG | 0.7 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Hardness | mg/L | NG | ≤ 200 | 76 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Iodide | mg/L | ≤ 0.5 | NG | 0.01 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Iron | mg/L | NG | ≤ 0.3 | 0.0026 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Lead | mg/L | ≤ 0.01 | NG | 0.0003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Magnesium | mg/L | NG | NG | 7.60 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | 0.0025 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0006 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | NDMA (N-Nitrosodimethylamine) | ng/L | ≤ 100 | NG | 24 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Nickel | mg/L | ≤ 0.02 | NG | 0.0009 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 1.34 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | pH | pH units | NG | 6.5 - 8.5 | 8.9 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Potassium | mg/L | NG | NG | 6.15 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Silica - reactive | mg/L | NG | ≤ 80 | 4.47 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Sodium | mg/L | NG | ≤ 180 | 47.3 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Sulphate | mg/L | NG | ≤ 250 | 61.6 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Total dissolved solids | mg/L | NG | ≤ 600 | 232 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Zinc | mg/L | NG | ≤ 3 | 0.0017 | NA | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Hardness - English Degrees | °e | NG | NG | 5.32 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Hardness - French Degrees | °f | NG | NG | 7.6 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Hardness - German Degrees | °dH | NG | NG | 4.26 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tailem Bend | Hardness - International | PPM or mg/L | NG | NG | 76 | NG | Chloramine / UV | 01/04/2022 - 31/03/2023
South East | Tarpeena | Alkalinity | mg/L | NG | NG | 366 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Aluminium - acid soluble | mg/L | NG | ≤ 0.2 | 0.002 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Antimony | mg/L | ≤ 0.003 | NG | <0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Arsenic | mg/L | ≤ 0.01 | NG | <0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Barium | mg/L | ≤ 2 | NG | 0.0468 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Beryllium | mg/L | ≤ 0.06 | NG | <0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Bicarbonate | mg/L | NG | NG | 446 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Boron | mg/L | ≤ 4 | NG | 0.068 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Cadmium | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Calcium | mg/L | NG | NG | 131 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Carbonate | mg/L | NG | NG | 0 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chloral hydrate | µg/L | ≤ 100 | NG | <1.0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chloride | mg/L | NG | ≤ 250 | 180 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chlorine (free residual) | mg/L | ≤ 5 | ≤ 0.6 | 0.9 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chlorite | mg/L | ≤ 0.8 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chloroacetic acid | µg/L | ≤ 150 | NG | <3 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Chromium | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Colour | HU | NG | ≤ 15 | <1 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Copper | mg/L | ≤ 2 | ≤ 1 | 0.0071 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Cyanide as CN | mg/L | ≤ 0.08 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Dichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | E. coli | cfu/100mL | 0 | NG | 0 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Fluoride | mg/L | ≤ 1.5 | NG | 0.2 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Hardness | mg/L | NG | ≤ 200 | 404 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Iodide | mg/L | ≤ 0.5 | NG | <0.01 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Iron | mg/L | NG | ≤ 0.3 | 0.0103 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Lanthanum | mg/L | ≤ 0.002 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Lead | mg/L | ≤ 0.01 | NG | 0.0005 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Magnesium | mg/L | NG | NG | 18.5 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Manganese | mg/L | ≤ 0.5 | ≤ 0.1 | < 0.001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Mercury | mg/L | ≤ 0.001 | NG | <0.00003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Molybdenum | mg/L | ≤ 0.05 | NG | 0.0003 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Nickel | mg/L | ≤ 0.02 | NG | 0.0002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Nitrate + nitrite as NO3 | mg/L | ≤ 50 | NG | 0.04 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Pentachlorophenol | µg/L | ≤ 10 | NG | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | pH | pH units | NG | 6.5 - 8.5 | 7.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Potassium | mg/L | NG | NG | 2.89 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Selenium | mg/L | ≤ 0.01 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Silica - reactive | mg/L | NG | ≤ 80 | 12.6 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Silver | mg/L | ≤ 0.1 | NG | <0.00002 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Sodium | mg/L | NG | ≤ 180 | 95.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Sulphate | mg/L | NG | ≤ 250 | 13.2 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Total dissolved solids | mg/L | NG | ≤ 600 | 699 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Trichloroacetic acid | µg/L | ≤ 100 | NG | <1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Trihalomethanes (THMs) | µg/L | ≤ 250 | NG | 51 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Turbidity | NTU | NG | ≤ 5 | <0.10 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Uranium | mg/L | ≤ 0.02 | NG | <0.0001 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Zinc | mg/L | NG | ≤ 3 | 0.0058 | NA | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | 2 4 6 Trichlorophenol | µg/L | ≤ 20 | ≤ 2 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | 2 4 Dichlorophenol | µg/L | ≤ 200 | ≤ 0.3 | <0.1 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | 2 Chlorophenol | µg/L | ≤ 300 | ≤ 0.1 | <0.05 | 100% | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Hardness - English Degrees | °e | NG | NG | 28.28 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Hardness - French Degrees | °f | NG | NG | 40.4 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Hardness - German Degrees | °dH | NG | NG | 22.62 | NG | Chlorine | 01/04/2022 - 31/03/2023
South East | Tarpeena | Hardness - International | PPM or mg/L | NG | NG | 404 | NG | Chlorine | 01/04/2022 - 31/03/2023
* Australian Drinking Water Guidelines (ADWG) - 2011
NA - Not Applicable
NG - No Guideline Value
# Prior to calculating compliance for health related chemicals, individual water sample test results are rounded to the same number of significant figures as the ADWG value (as prescribed in the ADWG and endorsed by SA Health).
# While we aim for 100 per cent health compliance all the time, the ADWG recognises exceedances in test results can happen occasionally. Most health guidelines for chemicals are based on a lifetime of exposure, therefore even if the compliance figures in this report are less than 100 per cent, it does not mean your water is not safe to drink. An exceedance of the health guideline is immediately investigated and corrective action can be taken, in conjunction with SA Health. Extensive testing by our water quality scientists is done to confirm South Australia’s drinking water is clean, good quality and safe to drink.
Disclaimer: While every effort has been made to ensure data is accurate, SA Water is not liable for any losses, damages, liabilities, claims and expenses relating to or arising from its provision (subject to any responsibility or liability implied by law which cannot be excluded). Where any responsibility or liability cannot by law be excluded, our liability is limited to us supplying corrected data, where available